## Site SCADA DNP
Message Structure
Message Type: | DNP 3.0 TCP/IP | Originating Device: | FS RTU | Destination Device: | SYS600 (MicroSCADA)
Port: | 20000 | Originating IP: | 192.168.1.248 | Destination IP: | 192.168.1.31
|  | Originating Subnet: | 255.255.255.0 | Destination Subnet: | 255.255.255.0
|  | Originating Gateway: |  | Destination Gateway:
|  | Originating ID: | 1 | Destination ID: | 100 (Slave Address)
DNP Map
Description | Source | Units | Dead Band | Format | DNP Address | Comment | ABB Comments | Testing Date | Testing Author
Analog Inputs
Feeder001.Rly.Sts.IA_A |  |  |  | 32 bit float | 30.5.0 | Correct | Corrected | 2017-12-20 | NJM
Feeder001.Rly.Sts.IB_A |  |  |  | 32 bit float | 30.5.1 |  |  | 2017-12-20 | NJM
Feeder001.Rly.Sts.IC_A |  |  |  | 32 bit float | 30.5.2 |  |  | 2017-12-20 | NJM
Feeder001.Rly.Sts.VAN_kV |  |  |  | 32 bit float | 30.5.3 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder001.Rly.Sts.VBN_kV |  |  |  | 32 bit float | 30.5.4 | Correct | Corrected | 2017-12-20 | NJM
Feeder001.Rly.Sts.VCN_kV |  |  |  | 32 bit float | 30.5.5 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder001.Rly.Sts.P_MW |  |  |  | 32 bit float | 30.5.6 | Correct |  | 2017-12-20 | NJM
Feeder001.Rly.Sts.Q_Mvar |  |  |  | 32 bit float | 30.5.7 | Correct |  | 2017-12-20 | NJM
Feeder001.Rly.Sts.Freq_Hz |  |  |  | 32 bit float | 30.5.8 |  |  | 2017-12-20 | NJM
Feeder002.Rly.Sts.IA_A |  |  |  | 32 bit float | 30.5.9 | Correct | Corrected | 2017-12-20 | NJM
Feeder002.Rly.Sts.IB_A |  |  |  | 32 bit float | 30.5.10 |  |  | 2017-12-20 | NJM
Feeder002.Rly.Sts.IC_A |  |  |  | 32 bit float | 30.5.11 |  |  | 2017-12-20 | NJM
Feeder002.Rly.Sts.VAN_kV |  |  |  | 32 bit float | 30.5.12 | Correct |  | 2017-12-20 | NJM
Feeder002.Rly.Sts.VBN_kV |  |  |  | 32 bit float | 30.5.13 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder002.Rly.Sts.VCN_kV |  |  |  | 32 bit float | 30.5.14 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder002.Rly.Sts.P_MW |  |  |  | 32 bit float | 30.5.15 | Correct |  | 2017-12-20 | NJM
Feeder002.Rly.Sts.Q_Mvar |  |  |  | 32 bit float | 30.5.16 | Correct | Corrected | 2017-12-20 | NJM
Feeder002.Rly.Sts.Freq_Hz |  |  |  | 32 bit float | 30.5.17 |  |  | 2017-12-20 | NJM
Feeder003.Rly.Sts.IA_A |  |  |  | 32 bit float | 30.5.18 | Correct | Corrected | 2017-12-20 | NJM
Feeder003.Rly.Sts.IB_A |  |  |  | 32 bit float | 30.5.19 |  |  | 2017-12-20 | NJM
Feeder003.Rly.Sts.IC_A |  |  |  | 32 bit float | 30.5.20 |  |  | 2017-12-20 | NJM
Feeder003.Rly.Sts.VAN_kV |  |  |  | 32 bit float | 30.5.21 | Correct |  | 2017-12-20 | NJM
Feeder003.Rly.Sts.VBN_kV |  |  |  | 32 bit float | 30.5.22 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder003.Rly.Sts.VCN_kV |  |  |  | 32 bit float | 30.5.23 | Correct | Corrected 1/22/2018 | 2017-12-20 | NJM
Feeder003.Rly.Sts.P_MW |  |  |  | 32 bit float | 30.5.24 |  |  | 2017-12-20 | NJM
Feeder003.Rly.Sts.Q_Mvar |  |  |  | 32 bit float | 30.5.25 |  | Corrected | 2017-12-20 | NJM
Feeder003.Rly.Sts.Freq_Hz |  |  |  | 32 bit float | 30.5.26 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.IA_A |  |  |  | 32 bit float | 30.5.27 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.IB_A |  |  |  | 32 bit float | 30.5.28 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.IC_A |  |  |  | 32 bit float | 30.5.29 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.VAN_kV |  |  |  | 32 bit float | 30.5.30 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.VBN_kV |  |  |  | 32 bit float | 30.5.31 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.VCN_kV |  |  |  | 32 bit float | 30.5.32 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.P_MW |  |  |  | 32 bit float | 30.5.33 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.Q_Mvar |  |  |  | 32 bit float | 30.5.34 |  |  | 2017-12-20 | NJM
Feeder004.Rly.Sts.Freq_Hz |  |  |  | 32 bit float | 30.5.35 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.P_kW |  |  |  | 32 bit float | 30.5.36 | Correct |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.37 | Correct |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.PF |  |  |  | 32 bit float | 30.5.38 | Correct |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.S_kVA |  |  |  | 32 bit float | 30.5.39 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.PRec_kWh |  |  |  | 32 bit float | 30.5.40 | Is this available? Request from FS PE | Energy has not be brought into SCADA | 2017-12-20 | NJM
PMCoopEnergy.Sts.PDel_kWh |  |  |  | 32 bit float | 30.5.41 | Is this available? Request from FS PE | Energy has not be brought into SCADA | 2017-12-20 | NJM
PMCoopEnergy.Sts.QRec_kvarh |  |  |  | 32 bit float | 30.5.42 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.QDel_kvarh |  |  |  | 32 bit float | 30.5.43 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VAN_kV |  |  |  | 32 bit float | 30.5.44 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VBN_kV |  |  |  | 32 bit float | 30.5.45 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VCN_kV |  |  |  | 32 bit float | 30.5.46 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.IA_A |  |  |  | 32 bit float | 30.5.47 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.IB_A |  |  |  | 32 bit float | 30.5.48 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.IC_A |  |  |  | 32 bit float | 30.5.49 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VAB_kV |  |  |  | 32 bit float | 30.5.50 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VBC_kV |  |  |  | 32 bit float | 30.5.51 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.VCA_kV |  |  |  | 32 bit float | 30.5.52 |  |  | 2017-12-20 | NJM
PMCoopEnergy.Sts.Freq_Hz |  |  |  | 32 bit float | 30.5.53 | Correct | Corrected | 2017-12-20 | NJM
PMCoopEnergy.Sts.VRMS_kV |  |  |  | 32 bit float | 30.5.54 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.55 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.56 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.57 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.58 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.59 |  |  | 2017-12-20 | NJM
PPC.Sts.QSp_Mvar |  |  |  | 32 bit float | 30.5.60 | Correct |  | 2017-12-20 | NJM
PPC.Sts.PFSp |  |  |  | 32 bit float | 30.5.61 | Correct |  | 2017-12-20 | NJM
PPC.Sts.Vsp_kV |  |  |  | 32 bit float | 30.5.62 | Correct |  | 2017-12-20 | NJM
PPC.Sts.Psp_MW |  |  |  | 32 bit float | 30.5.63 | Correct |  | 2017-12-20 | NJM
PPC.Sts.PRampUp_MWMin |  |  |  | 32 bit float | 30.5.64 |  |  | 2017-12-20 | NJM
PPC.Sts.PRampDown_MWMin |  |  |  | 32 bit float | 30.5.65 |  |  | 2017-12-20 | NJM
PPC.Sts.QRampUp_MWMin |  |  |  | 32 bit float | 30.5.66 |  |  | 2017-12-20 | NJM
PPC.Sts.QRampDown_MWMin |  |  |  | 32 bit float | 30.5.67 |  |  | 2017-12-20 | NJM
PPC.Sts.QCntrlMode (0=Reactive, 1=Voltage, 2=PF) |  |  |  | 32 bit float | 30.5.68 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.69 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.70 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.71 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.72 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.73 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.74 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.75 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.76 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.77 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.78 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.79 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.80 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.81 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.82 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.83 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.84 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.85 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.86 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.87 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.88 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.89 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.90 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.91 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.92 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.93 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.94 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.95 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.96 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.97 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.98 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.99 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.100 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.101 | Correct |  | 2017-12-20 | NJM
PCS001.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.102 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.103 | Correct | Corrected | 2017-12-20 | NJM
PCS001.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.104 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.105 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.106 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.107 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.108 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.109 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.110 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.111 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.112 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.113 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.114 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.115 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.116 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.117 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.118 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.119 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.120 | Correct |  | 2017-12-20 | NJM
PCS001.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.121 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.122 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.123 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.124 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.125 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.126 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.127 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.128 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.129 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.130 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.131 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.132 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.133 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.134 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.135 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.136 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.137 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.138 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.139 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.140 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.141 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.142 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.143 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.144 | Correct |  | 2017-12-20 | NJM
PCS002.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.145 |  |  | 2017-12-20 | NJM
PCS002.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.146 | Correct | Corrected | 2017-12-20 | NJM
PCS002.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.147 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.148 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.149 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.150 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.151 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.152 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.153 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.154 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.155 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.156 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.157 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.158 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.159 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.160 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.161 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.162 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.163 | Correct |  | 2017-12-20 | NJM
PCS002.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.164 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.165 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.166 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.167 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.168 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.169 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.170 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.171 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.172 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.173 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.174 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.175 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.176 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.177 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.178 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.179 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.180 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.181 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.182 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.183 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.184 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.185 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.186 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.187 | Correct |  | 2017-12-20 | NJM
PCS003.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.188 |  |  | 2017-12-20 | NJM
PCS003.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.189 | Correct | Corrected | 2017-12-20 | NJM
PCS003.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.190 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.191 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.192 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.193 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.194 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.195 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.196 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.197 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.198 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.199 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.200 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.201 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.202 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.203 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.204 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.205 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.206 | Correct |  | 2017-12-20 | NJM
PCS003.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.207 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.208 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.209 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.210 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.211 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.212 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.213 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.214 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.215 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.216 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.217 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.218 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.219 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.220 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.221 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.222 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.223 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.224 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.225 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.226 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.227 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.228 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.229 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.230 | Correct |  | 2017-12-20 | NJM
PCS004.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.231 |  |  | 2017-12-20 | NJM
PCS004.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.232 | Correct | Corrected | 2017-12-20 | NJM
PCS004.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.233 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.234 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.235 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.236 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.237 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.238 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.239 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.240 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.241 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.242 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.243 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.244 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.245 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.246 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.247 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.248 | Correct |  | 2017-12-20 | NJM
PCS004.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.249 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.250 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.251 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.252 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.253 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.254 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.255 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.256 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.257 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.258 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.259 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.260 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.261 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.262 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.263 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.264 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.265 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.266 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.267 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.268 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.269 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.270 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.271 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.272 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.273 | Correct |  | 2017-12-20 | NJM
PCS005.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.274 |  |  | 2017-12-20 | NJM
PCS005.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.275 | Correct | Corrected | 2017-12-20 | NJM
PCS005.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.276 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.277 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.278 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.279 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.280 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.281 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.282 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.283 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.284 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.285 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.286 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.287 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.288 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.289 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.290 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.291 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.292 | Correct |  | 2017-12-20 | NJM
PCS005.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.293 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.294 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.295 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.296 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.297 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.298 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.299 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.300 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.301 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.302 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.303 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.304 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.305 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.306 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.307 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.308 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.309 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.310 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.311 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.312 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.313 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.314 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.315 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.316 | Correct |  | 2017-12-20 | NJM
PCS006.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.317 |  |  | 2017-12-20 | NJM
PCS006.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.318 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.319 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.320 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.321 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.322 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.323 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.324 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.325 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.326 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.327 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.328 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.329 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.330 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.331 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.332 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.333 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.334 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.335 | Correct |  | 2017-12-20 | NJM
PCS006.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.336 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.337 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.338 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.339 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.340 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.341 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.342 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.343 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.344 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.345 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.346 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.347 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.348 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.349 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.350 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.351 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.352 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.353 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.354 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.355 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.356 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.357 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.358 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.359 | Correct |  | 2017-12-20 | NJM
PCS007.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.360 |  |  | 2017-12-20 | NJM
PCS007.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.361 | Correct | Corrected | 2017-12-20 | NJM
PCS007.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.362 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.363 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.364 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.365 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.366 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.367 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.368 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.369 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.370 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.371 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.372 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.373 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.374 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.375 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.376 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.377 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.378 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.379 | Correct |  | 2017-12-20 | NJM
PCS007.DCCT019.Sts.IA_A |  |  |  | 32 bit float | 30.5.380 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.381 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.382 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.383 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.384 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.385 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.386 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.387 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.388 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.389 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.390 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.391 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.392 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.393 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.394 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.395 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.396 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.397 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.398 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.399 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.400 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.401 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.402 | Correct |  | 2017-12-20 | NJM
PCS008.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.403 |  |  | 2017-12-20 | NJM
PCS008.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.404 | Correct | Corrected | 2017-12-20 | NJM
PCS008.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.405 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.406 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.407 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.408 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.409 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.410 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.411 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.412 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.413 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.414 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.415 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.416 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.417 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.418 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.419 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.420 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.421 | Correct |  | 2017-12-20 | NJM
PCS008.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.422 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.423 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.424 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.425 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.426 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.427 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.428 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.429 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.430 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.431 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.432 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.433 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.434 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.435 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.436 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.437 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.438 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.439 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.440 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.441 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.442 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.443 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.444 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.445 | Correct |  | 2017-12-20 | NJM
PCS009.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.446 |  |  | 2017-12-20 | NJM
PCS009.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.447 | Correct | Corrected | 2017-12-20 | NJM
PCS009.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.448 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.449 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.450 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.451 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.452 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.453 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.454 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.455 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.456 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.457 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.458 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.459 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.460 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.461 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.462 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.463 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.464 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.465 | Correct |  | 2017-12-20 | NJM
PCS009.DCCT019.Sts.IA_A |  |  |  | 32 bit float | 30.5.466 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.467 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.468 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.469 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.470 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.471 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.472 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.473 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.474 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.475 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.476 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.477 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.478 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.479 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.480 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.481 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.482 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.483 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.484 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.485 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.486 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.487 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.488 | Correct |  | 2017-12-20 | NJM
PCS010.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.489 |  |  | 2017-12-20 | NJM
PCS010.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.490 | Correct | Corrected | 2017-12-20 | NJM
PCS010.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.491 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.492 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.493 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.494 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.495 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.496 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.497 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.498 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.499 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.500 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.501 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.502 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.503 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.504 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.505 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.506 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.507 | Correct |  | 2017-12-20 | NJM
PCS010.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.508 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.509 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.510 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.511 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.512 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.513 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.514 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.515 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.516 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.517 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.518 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.519 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.520 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.521 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.522 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.523 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.524 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.525 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.526 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.527 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.528 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.529 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.530 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.531 | Correct |  | 2017-12-20 | NJM
PCS011.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.532 |  |  | 2017-12-20 | NJM
PCS011.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.533 | Correct | Corrected | 2017-12-20 | NJM
PCS011.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.534 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.535 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.536 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.537 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.538 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.539 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.540 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.541 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.542 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.543 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.544 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.545 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.546 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.547 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.548 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.549 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.550 | Correct |  | 2017-12-20 | NJM
PCS011.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.551 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.552 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.553 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.554 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.555 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.556 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.557 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.558 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.559 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.560 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.561 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.562 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.563 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.564 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.565 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.566 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.567 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.568 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.569 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.570 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.571 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.572 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.573 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.574 | Correct |  | 2017-12-20 | NJM
PCS012.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.575 |  |  | 2017-12-20 | NJM
PCS012.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.576 | Correct | Corrected | 2017-12-20 | NJM
PCS012.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.577 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.578 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.579 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.580 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.581 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.582 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.583 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.584 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.585 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.586 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.587 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.588 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.589 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.590 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.591 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.592 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.593 | Correct |  | 2017-12-20 | NJM
PCS012.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.594 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.595 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.596 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.597 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.598 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.599 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.600 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.601 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.602 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.603 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.604 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.605 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.606 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.607 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.608 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.609 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.610 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.611 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.612 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.613 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.614 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.615 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.616 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.617 | Correct |  | 2017-12-20 | NJM
PCS013.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.618 |  |  | 2017-12-20 | NJM
PCS013.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.619 | Correct | Corrected | 2017-12-20 | NJM
PCS013.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.620 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.621 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.622 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.623 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.624 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.625 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.626 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.627 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.628 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.629 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.630 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.631 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.632 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.633 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.634 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.635 | Correct |  | 2017-12-20 | NJM
PCS013.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.636 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.637 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.638 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.639 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.640 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.641 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.642 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.643 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.644 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.645 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.646 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.647 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.648 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.649 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.650 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.651 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.652 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.653 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.654 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.655 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.656 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.657 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.658 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.659 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.660 | Correct |  | 2017-12-20 | NJM
PCS014.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.661 |  |  | 2017-12-20 | NJM
PCS014.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.662 | Correct | Corrected | 2017-12-20 | NJM
PCS014.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.663 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.664 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.665 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.666 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.667 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.668 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.669 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.670 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.671 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.672 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.673 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.674 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.675 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.676 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.677 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.678 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.679 | Correct |  | 2017-12-20 | NJM
PCS014.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.680 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.681 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.682 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.683 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.684 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.685 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.686 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.687 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.688 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.689 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.690 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.691 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.692 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.693 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.694 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.695 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.696 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.697 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.698 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.699 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.700 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.701 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.702 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.703 | Correct |  | 2017-12-20 | NJM
PCS015.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.704 |  |  | 2017-12-20 | NJM
PCS015.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.705 | Correct | Corrected | 2017-12-20 | NJM
PCS015.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.706 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.707 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.708 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.709 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.710 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.711 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.712 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.713 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.714 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.715 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.716 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.717 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.718 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.719 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.720 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.721 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.722 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.723 | Correct |  | 2017-12-20 | NJM
PCS015.DCCT019.Sts.IA_A |  |  |  | 32 bit float | 30.5.724 |  | Corrected | 2017-12-20 | NJM
PCS015.DCCT020.Sts.IA_A |  |  |  | 32 bit float | 30.5.725 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.726 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.727 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.728 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.729 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.730 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.731 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.732 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.733 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.734 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.735 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.736 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.737 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.738 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.739 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.740 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.741 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.742 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.743 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.744 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.745 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.746 | Correct |  | 2017-12-20 | NJM
PCS016.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.747 |  |  | 2017-12-20 | NJM
PCS016.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.748 | Correct | Corrected | 2017-12-20 | NJM
PCS016.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.749 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.750 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.751 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.752 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.753 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.754 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.755 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.756 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.757 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.758 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.759 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.760 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.761 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.762 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.763 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.764 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.765 | Correct |  | 2017-12-20 | NJM
PCS016.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.766 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.767 |  | Corrected | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.768 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.769 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.770 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.771 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.772 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.773 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.774 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.775 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.776 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.777 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.778 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.779 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.780 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.781 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.782 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.783 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.784 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.785 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.786 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.787 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.788 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.789 | Correct |  | 2017-12-20 | NJM
PCS017.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.790 |  |  | 2017-12-20 | NJM
PCS017.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.791 | Correct | Corrected | 2017-12-20 | NJM
PCS017.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.792 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.793 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.794 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.795 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.796 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.797 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.798 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.799 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.800 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.801 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.802 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.803 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.804 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.805 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.806 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.807 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.808 | Correct |  | 2017-12-20 | NJM
PCS017.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.809 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.810 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.811 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.812 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.813 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.814 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.815 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.816 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.817 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.818 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.819 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.820 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.821 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.822 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.823 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.824 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.825 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.826 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.827 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.828 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.829 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.830 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.831 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.832 | Correct |  | 2017-12-20 | NJM
PCS018.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.833 |  |  | 2017-12-20 | NJM
PCS018.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.834 | Correct | Corrected | 2017-12-20 | NJM
PCS018.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.835 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.836 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.837 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.838 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.839 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.840 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.841 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.842 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.843 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.844 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.845 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.846 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.847 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.848 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.849 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.850 | Correct |  | 2017-12-20 | NJM
PCS018.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.851 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.852 |  | Corrected | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.853 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.854 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.855 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.856 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.857 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.858 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.859 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.860 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.861 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.862 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.863 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.864 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.865 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.866 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.867 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.868 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.869 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.870 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.871 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.872 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.873 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.874 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.875 | Correct |  | 2017-12-20 | NJM
PCS019.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.876 |  |  | 2017-12-20 | NJM
PCS019.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.877 | Correct | Corrected | 2017-12-20 | NJM
PCS019.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.878 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.879 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.880 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.881 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.882 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.883 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.884 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.885 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.886 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.887 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.888 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.889 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.890 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.891 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.892 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.893 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.894 | Correct |  | 2017-12-20 | NJM
PCS019.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.895 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.896 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.897 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.898 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.899 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.900 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.901 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.902 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.903 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.904 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.905 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.906 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.907 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.908 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.909 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.910 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.911 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.912 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.913 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.914 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.915 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.916 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.917 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.918 | Correct |  | 2017-12-20 | NJM
PCS020.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.919 |  |  | 2017-12-20 | NJM
PCS020.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.920 | Correct | Corrected | 2017-12-20 | NJM
PCS020.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.921 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.922 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.923 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.924 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.925 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.926 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.927 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.928 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.929 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.930 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.931 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.932 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.933 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.934 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.935 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.936 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.937 | Correct |  | 2017-12-20 | NJM
PCS020.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.938 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.939 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.940 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.941 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.942 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.943 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.944 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.945 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.946 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.947 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.948 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.949 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.950 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.951 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.952 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.953 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.954 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.955 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.956 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.957 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.958 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.959 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.960 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.961 | Correct |  | 2017-12-20 | NJM
PCS021.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.962 |  |  | 2017-12-20 | NJM
PCS021.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.963 | Correct | Corrected | 2017-12-20 | NJM
PCS021.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.964 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.965 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.966 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.967 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.968 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.969 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.970 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.971 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.972 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.973 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.974 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.975 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.976 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.977 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.978 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.979 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.980 | Correct |  | 2017-12-20 | NJM
PCS021.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.981 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.982 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.983 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.984 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.985 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.986 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.987 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.988 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.989 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.990 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.991 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.992 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.993 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.994 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.995 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.996 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.997 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.998 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.999 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.1000 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.1001 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.1002 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.1003 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.1004 | Correct |  | 2017-12-20 | NJM
PCS022.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.1005 |  |  | 2017-12-20 | NJM
PCS022.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.1006 | Correct | Corrected | 2017-12-20 | NJM
PCS022.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.1007 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.1008 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.1009 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.1010 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.1011 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.1012 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.1013 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.1014 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.1015 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.1016 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.1017 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.1018 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.1019 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.1020 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.1021 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.1022 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.1023 | Correct |  | 2017-12-20 | NJM
PCS022.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.1024 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1025 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1026 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1027 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.P_kW |  |  |  | 32 bit float | 30.5.1028 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1029 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.Q_kvar |  |  |  | 32 bit float | 30.5.1030 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.S_kVA |  |  |  | 32 bit float | 30.5.1031 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.PSp_Pct |  |  |  | 32 bit float | 30.5.1032 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.QSp_kvar |  |  |  | 32 bit float | 30.5.1033 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.PFSp |  |  |  | 32 bit float | 30.5.1034 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VSp_V |  |  |  | 32 bit float | 30.5.1035 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.PDC_kW |  |  |  | 32 bit float | 30.5.1036 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.IDC_A |  |  |  | 32 bit float | 30.5.1037 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VDC_V |  |  |  | 32 bit float | 30.5.1038 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VAN_V |  |  |  | 32 bit float | 30.5.1039 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VBN_V |  |  |  | 32 bit float | 30.5.1040 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VCN_V |  |  |  | 32 bit float | 30.5.1041 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VAB_V |  |  |  | 32 bit float | 30.5.1042 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VBC_V |  |  |  | 32 bit float | 30.5.1043 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.VCA_V |  |  |  | 32 bit float | 30.5.1044 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.IA_A |  |  |  | 32 bit float | 30.5.1045 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.IB_A |  |  |  | 32 bit float | 30.5.1046 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.IC_A |  |  |  | 32 bit float | 30.5.1047 | Correct |  | 2017-12-20 | NJM
PCS023.InvA.Sts.OpState |  |  |  | 32 bit float | 30.5.1048 |  |  | 2017-12-20 | NJM
PCS023.InvA.Sts.FltState |  |  |  | 32 bit float | 30.5.1049 | Correct | Corrected | 2017-12-20 | NJM
PCS023.DCCT001.Sts.IA_A |  |  |  | 32 bit float | 30.5.1050 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT002.Sts.IA_A |  |  |  | 32 bit float | 30.5.1051 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT003.Sts.IA_A |  |  |  | 32 bit float | 30.5.1052 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT004.Sts.IA_A |  |  |  | 32 bit float | 30.5.1053 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT005.Sts.IA_A |  |  |  | 32 bit float | 30.5.1054 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT006.Sts.IA_A |  |  |  | 32 bit float | 30.5.1055 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT007.Sts.IA_A |  |  |  | 32 bit float | 30.5.1056 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT008.Sts.IA_A |  |  |  | 32 bit float | 30.5.1057 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT009.Sts.IA_A |  |  |  | 32 bit float | 30.5.1058 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT010.Sts.IA_A |  |  |  | 32 bit float | 30.5.1059 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT011.Sts.IA_A |  |  |  | 32 bit float | 30.5.1060 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT012.Sts.IA_A |  |  |  | 32 bit float | 30.5.1061 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT013.Sts.IA_A |  |  |  | 32 bit float | 30.5.1062 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT014.Sts.IA_A |  |  |  | 32 bit float | 30.5.1063 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT015.Sts.IA_A |  |  |  | 32 bit float | 30.5.1064 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT016.Sts.IA_A |  |  |  | 32 bit float | 30.5.1065 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT017.Sts.IA_A |  |  |  | 32 bit float | 30.5.1066 | Correct |  | 2017-12-20 | NJM
PCS023.DCCT018.Sts.IA_A |  |  |  | 32 bit float | 30.5.1067 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1068 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1069 |  | Not Used | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1070 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1071 |  |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1072 |  |  | 2017-12-20 | NJM
MET001.Sts.AirTemp_C |  |  |  | 32 bit float | 30.5.1073 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.RelHum_Pct |  |  |  | 32 bit float | 30.5.1074 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.AirPress_mBar |  |  |  | 32 bit float | 30.5.1075 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.WindSpd_mps |  |  |  | 32 bit float | 30.5.1076 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.WindDir_Deg |  |  |  | 32 bit float | 30.5.1077 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.RainFallTot_mm |  |  |  | 32 bit float | 30.5.1078 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.MST001.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1079 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.MST002.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1080 | Bad Quality - Also Bad Quality in Site SCADA | Harware issue | 2017-12-20 | NJM
MET001.Sts.GHIrr_Wm2 |  |  |  | 32 bit float | 30.5.1081 | Correct |  | 2017-12-20 | NJM
MET001.Sts.POAIrr_Wm2 |  |  |  | 32 bit float | 30.5.1082 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1083 |  |  | 2017-12-20 | NJM
MET002.Sts.AirTemp_C |  |  |  | 32 bit float | 30.5.1084 | Correct |  | 2017-12-20 | NJM
MET002.Sts.RelHum_Pct |  |  |  | 32 bit float | 30.5.1085 | Correct |  | 2017-12-20 | NJM
MET002.Sts.AirPress_mBar |  |  |  | 32 bit float | 30.5.1086 | Correct |  | 2017-12-20 | NJM
MET002.Sts.WindSpd_mps |  |  |  | 32 bit float | 30.5.1087 | Correct |  | 2017-12-20 | NJM
MET002.Sts.WindDir_Deg |  |  |  | 32 bit float | 30.5.1088 | Correct |  | 2017-12-20 | NJM
MET002.Sts.RainFallTot_mm |  |  |  | 32 bit float | 30.5.1089 | Correct |  | 2017-12-20 | NJM
MET002.MST001.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1090 | Correct |  | 2017-12-20 | NJM
MET002.MST002.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1091 | Correct |  | 2017-12-20 | NJM
MET002.Sts.GHIrr_Wm2 |  |  |  | 32 bit float | 30.5.1092 | Correct |  | 2017-12-20 | NJM
MET002.Sts.POAIrr_Wm2 |  |  |  | 32 bit float | 30.5.1093 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1094 |  |  | 2017-12-20 | NJM
MET003.Sts.AirTemp_C |  |  |  | 32 bit float | 30.5.1095 | Correct |  | 2017-12-20 | NJM
MET003.Sts.RelHum_Pct |  |  |  | 32 bit float | 30.5.1096 | Correct |  | 2017-12-20 | NJM
MET003.Sts.AirPress_mBar |  |  |  | 32 bit float | 30.5.1097 | Correct |  | 2017-12-20 | NJM
MET003.Sts.WindSpd_mps |  |  |  | 32 bit float | 30.5.1098 | Correct |  | 2017-12-20 | NJM
MET003.Sts.WindDir_Deg |  |  |  | 32 bit float | 30.5.1099 | Correct |  | 2017-12-20 | NJM
MET003.Sts.RainFallTot_mm |  |  |  | 32 bit float | 30.5.1100 | Correct |  | 2017-12-20 | NJM
MET003.MST001.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1101 | Correct |  | 2017-12-20 | NJM
MET003.MST002.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1102 | Correct |  | 2017-12-20 | NJM
MET003.Sts.GHIrr_Wm2 |  |  |  | 32 bit float | 30.5.1103 | Correct |  | 2017-12-20 | NJM
MET003.Sts.POAIrr_Wm2 |  |  |  | 32 bit float | 30.5.1104 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1105 |  |  | 2017-12-20 | NJM
MET004.Sts.AirTemp_C |  |  |  | 32 bit float | 30.5.1106 | Correct |  | 2017-12-20 | NJM
MET004.Sts.RelHum_Pct |  |  |  | 32 bit float | 30.5.1107 | Correct |  | 2017-12-20 | NJM
MET004.Sts.AirPress_mBar |  |  |  | 32 bit float | 30.5.1108 | Correct |  | 2017-12-20 | NJM
MET004.Sts.WindSpd_mps |  |  |  | 32 bit float | 30.5.1109 | Correct |  | 2017-12-20 | NJM
MET004.Sts.WindDir_Deg |  |  |  | 32 bit float | 30.5.1110 | Correct |  | 2017-12-20 | NJM
MET004.Sts.RainFallTot_mm |  |  |  | 32 bit float | 30.5.1111 | Correct |  | 2017-12-20 | NJM
MET004.MST001.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1112 | Correct |  | 2017-12-20 | NJM
MET004.MST002.Sts.Temp_C |  |  |  | 32 bit float | 30.5.1113 | Correct |  | 2017-12-20 | NJM
MET004.Sts.GHIrr_Wm2 |  |  |  | 32 bit float | 30.5.1114 | Correct |  | 2017-12-20 | NJM
MET004.Sts.POAIrr_Wm2 |  |  |  | 32 bit float | 30.5.1115 | Correct |  | 2017-12-20 | NJM
Spare |  |  |  | 32 bit float | 30.5.1116 |  |  | 2017-12-20 | NJM
PCS001.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1117 | Correct | Corrected | 2017-12-20 | NJM
PCS001.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1118 | Correct | Corrected | 2017-12-20 | NJM
PCS001.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1119 | Correct | Corrected | 2017-12-20 | NJM
PCS002.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1120 | Correct | Corrected | 2017-12-20 | NJM
PCS002.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1121 | Correct | Corrected | 2017-12-20 | NJM
PCS002.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1122 | Correct | Corrected | 2017-12-20 | NJM
PCS003.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1123 | Correct | Corrected | 2017-12-20 | NJM
PCS003.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1124 | Correct | Corrected | 2017-12-20 | NJM
PCS003.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1125 | Correct | Corrected | 2017-12-20 | NJM
PCS004.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1126 | Correct | Corrected | 2017-12-20 | NJM
PCS004.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1127 | Correct | Corrected | 2017-12-20 | NJM
PCS004.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1128 | Correct | Corrected | 2017-12-20 | NJM
PCS005.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1129 | Correct | Corrected | 2017-12-20 | NJM
PCS005.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1130 | Correct | Corrected | 2017-12-20 | NJM
PCS005.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1131 | Correct | Corrected | 2017-12-20 | NJM
PCS006.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1132 | Correct | Corrected | 2017-12-20 | NJM
PCS006.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1133 | Correct | Corrected | 2017-12-20 | NJM
PCS006.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1134 | Correct | Corrected | 2017-12-20 | NJM
PCS007.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1135 | Correct | Corrected | 2017-12-20 | NJM
PCS007.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1136 | Correct | Corrected | 2017-12-20 | NJM
PCS007.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1137 | Correct | Corrected | 2017-12-20 | NJM
PCS008.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1138 | Correct | Corrected | 2017-12-20 | NJM
PCS008.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1139 | Correct | Corrected | 2017-12-20 | NJM
PCS008.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1140 | Correct | Corrected | 2017-12-20 | NJM
PCS009.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1141 | Correct | Corrected | 2017-12-20 | NJM
PCS009.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1142 | Correct | Corrected | 2017-12-20 | NJM
PCS009.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1143 | Correct | Corrected | 2017-12-20 | NJM
PCS010.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1144 | Correct | Corrected | 2017-12-20 | NJM
PCS010.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1145 | Correct | Corrected | 2017-12-20 | NJM
PCS010.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1146 | Correct | Corrected | 2017-12-20 | NJM
PCS011.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1147 | Correct | Corrected | 2017-12-20 | NJM
PCS011.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1148 | Correct | Corrected | 2017-12-20 | NJM
PCS011.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1149 | Correct | Corrected | 2017-12-20 | NJM
PCS012.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1150 | Correct | Corrected | 2017-12-20 | NJM
PCS012.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1151 | Correct | Corrected | 2017-12-20 | NJM
PCS012.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1152 | Correct | Corrected | 2017-12-20 | NJM
PCS013.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1153 | Correct | Corrected | 2017-12-20 | NJM
PCS013.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1154 | Correct | Corrected | 2017-12-20 | NJM
PCS013.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1155 | Correct | Corrected | 2017-12-20 | NJM
PCS014.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1156 | Correct | Corrected | 2017-12-20 | NJM
PCS014.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1157 | Correct | Corrected | 2017-12-20 | NJM
PCS014.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1158 | Correct | Corrected | 2017-12-20 | NJM
PCS015.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1159 | Correct | Corrected | 2017-12-20 | NJM
PCS015.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1160 | Correct | Corrected | 2017-12-20 | NJM
PCS015.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1161 | Correct | Corrected | 2017-12-20 | NJM
PCS016.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1162 | Correct | Corrected | 2017-12-20 | NJM
PCS016.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1163 | Correct | Corrected | 2017-12-20 | NJM
PCS016.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1164 | Correct | Corrected | 2017-12-20 | NJM
PCS017.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1165 | Correct | Corrected | 2017-12-20 | NJM
PCS017.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1166 | Correct | Corrected | 2017-12-20 | NJM
PCS017.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1167 | Correct | Corrected | 2017-12-20 | NJM
PCS018.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1168 | Correct | Corrected | 2017-12-20 | NJM
PCS018.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1169 | Correct | Corrected | 2017-12-20 | NJM
PCS018.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1170 | Correct | Corrected | 2017-12-20 | NJM
PCS019.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1171 | Correct | Corrected | 2017-12-20 | NJM
PCS019.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1172 | Correct | Corrected | 2017-12-20 | NJM
PCS019.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1173 | Correct | Corrected | 2017-12-20 | NJM
PCS020.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1174 | Correct | Corrected | 2017-12-20 | NJM
PCS020.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1175 | Correct | Corrected | 2017-12-20 | NJM
PCS020.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1176 | Correct | Corrected | 2017-12-20 | NJM
PCS021.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1177 | Correct | Corrected | 2017-12-20 | NJM
PCS021.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1178 | Correct | Corrected | 2017-12-20 | NJM
PCS021.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1179 | Correct | Corrected | 2017-12-20 | NJM
PCS022.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1180 | Correct | Corrected | 2017-12-20 | NJM
PCS022.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1181 | Correct | Corrected | 2017-12-20 | NJM
PCS022.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1182 | Correct | Corrected | 2017-12-20 | NJM
PCS023.InvA.Sts.PRecTot_kWh |  | MWh |  | 32 bit float | 30.5.1183 | Correct | Corrected | 2017-12-20 | NJM
PCS023.InvA.Sts.PRec_kWh |  | MWh |  | 32 bit float | 30.5.1184 | Correct | Corrected | 2017-12-20 | NJM
PCS023.InvA.Sts.PDel_kWh |  | MWh |  | 32 bit float | 30.5.1185 | Correct | Corrected | 2017-12-20 | NJM
Binary Inputs
Feeder001.CB.Sts.Clsd |  | n/a |  | binary input | 1.1.0 | Correct
Feeder001.DisconnectSw001.Sts.Clsd |  | n/a |  | binary input | 1.0.1
Feeder001.DisconnectSw002.Sts.Clsd |  | n/a |  | binary input | 1.0.2
Feeder001.DisconnectSw003.Sts.Clsd |  | n/a |  | binary input | 1.0.3
Feeder001.Rly.Alm.Comm (Communication Alarm) |  | n/a |  | binary input | 1.0.4 | Correct
Feeder001.Rly.Alm.Flt (Relay Unhealthy) |  | n/a |  | binary input | 1.0.5
Feeder001.Alm.Trp |  | n/a |  | binary input | 1.1.6
Feeder002.CB.Sts.Clsd |  | n/a |  | binary input | 1.1.7 | Correct
Feeder002.DisconnectSw001.Sts.Clsd |  | n/a |  | binary input | 1.0.8
Feeder002.DisconnectSw002.Sts.Clsd |  | n/a |  | binary input | 1.0.9
Feeder002.DisconnectSw003.Sts.Clsd |  | n/a |  | binary input | 1.0.10
Feeder002.Rly.Alm.Comm (Communication Alarm) |  | n/a |  | binary input | 1.0.11 | Correct | Corrected
Feeder002.Rly.Alm.Flt (Relay Unhealthy) |  | n/a |  | binary input | 1.0.12
Feeder002.Alm.Trp |  | n/a |  | binary input | 1.1.13
Feeder003.CB.Sts.Clsd |  | n/a |  | binary input | 1.1.14 | Correct
Feeder003.DisconnectSw001.Sts.Clsd |  | n/a |  | binary input | 1.0.15
Feeder003.DisconnectSw002.Sts.Clsd |  | n/a |  | binary input | 1.0.16
Feeder003.DisconnectSw003.Sts.Clsd |  | n/a |  | binary input | 1.0.17
Feeder003.Rly.Alm.Comm (Communication Alarm) |  | n/a |  | binary input | 1.0.18 | Correct | Corrected
Feeder003.Rly.Alm.Flt (Relay Unhealthy) |  | n/a |  | binary input | 1.0.19
Feeder003.Alm.Trp |  | n/a |  | binary input | 1.1.20
Feeder004.CB.Sts.Clsd |  | n/a |  | binary input | 1.0.21
Feeder004.DisconnectSw001.Sts.Clsd |  | n/a |  | binary input | 1.0.22
Feeder004.DisconnectSw002.Sts.Clsd |  | n/a |  | binary input | 1.0.23
Feeder004.DisconnectSw003.Sts.Clsd |  | n/a |  | binary input | 1.0.24
Feeder004.Rly.Alm.Comm (Communication Alarm) |  | n/a |  | binary input | 1.0.25
Feeder004.Rly.Alm.Flt (Relay Unhealthy) |  | n/a |  | binary input | 1.0.26
CapSw001.Sts.Clsd |  | n/a |  | binary input | 1.0.27 | Correct
CapSw002.Sts.Clsd |  | n/a |  | binary input | 1.0.28 | Correct
PMCoopEnergy.Alm.Comm (Communication Alarm) |  | n/a |  | binary input | 1.1.29 | Correct | Corrected
CBGFS372.Sts.Clsd |  | n/a |  | binary input | 1.0.30
CB52-3240.Sts.Clsd |  | n/a |  | binary input | 1.0.31
CB52-3243.Sts.Clsd |  | n/a |  | binary input | 1.0.32
CB52-3253.Sts.Clsd |  | n/a |  | binary input | 1.0.33
U1.Alm.XFMR |  | n/a |  | binary input | 1.0.34
Spare |  | n/a |  | binary input | 1.0.35
Spare |  | n/a |  | binary input | 1.0.36
Spare |  | n/a |  | binary input | 1.0.37
Spare |  | n/a |  | binary input | 1.0.38
PPC.Sts.PCntrlEn |  | n/a |  | binary input | 1.0.39 | Active power control enabled | Corrected 1/23/2018
PPC.Sts.PCntrlDis |  | n/a |  | binary input | 1.0.40 | Active power control disabled | Corrected 1/23/2018
PPC.Sts.PLclCntrlEn |  | n/a |  | binary input | 1.0.41 | Active power control from local (SCADA | Corrected 1/23/2018
PPC.Sts.PRemCntrlEn |  | n/a |  | binary input | 1.0.42 | Active power control from remote (TSO) | Corrected 1/23/2018
PPC.Sts.PPriorityEn |  | n/a |  | binary input | 1.0.43 | P Priority | Corrected 1/23/2018
PPC.Sts.QCntrlEn |  | n/a |  | binary input | 1.0.44 | Reactive power control enabled | Corrected 1/23/2018
PPC.Sts.QCntrlDis |  | n/a |  | binary input | 1.0.45 | Reactive power control disabled | Corrected 1/23/2018
PPC.Sts.QLclCntrlEn |  | n/a |  | binary input | 1.0.46 | Reactive power control from local(SCADA) | Corrected 1/23/2018
PPC.Sts.QRemCntrlEn |  | n/a |  | binary input | 1.0.47 | Reactive power control from remote(TSO) | Corrected 1/23/2018
PPC.Sts.QPriorityEn |  | n/a |  | binary input | 1.0.48 | Q priority
Spare |  | n/a |  | binary input | 1.0.49
PCS001.Alm.Control |  | n/a |  | binary input | 1.0.50
PCS001.Alm.Derate |  | n/a |  | binary input | 1.0.51
PCS001.Alm.Cooling |  | n/a |  | binary input | 1.0.52
PCS001.Alm.Offline |  | n/a |  | binary input | 1.0.53
PCS001.Alm.Comm |  | n/a |  | binary input | 1.0.54
PCS001.Alm.EPO |  | n/a |  | binary input | 1.0.55
PCS001.Sts.CBMain |  | n/a |  | binary input | 1.0.56
PCS001.Sts.PAuto |  | n/a |  | binary input | 1.0.57 | Correct
PCS001.Sts.QAuto |  | n/a |  | binary input | 1.0.58 | Correct
PCS001.Sts.Auto |  | n/a |  | binary input | 1.0.59
PCS002.Alm.Control |  | n/a |  | binary input | 1.0.60
PCS002.Alm.Derate |  | n/a |  | binary input | 1.0.61
PCS002.Alm.Cooling |  | n/a |  | binary input | 1.0.62
PCS002.Alm.Offline |  | n/a |  | binary input | 1.0.63
PCS002.Alm.Comm |  | n/a |  | binary input | 1.0.64
PCS002.Alm.EPO |  | n/a |  | binary input | 1.0.65
PCS002.Sts.CBMain |  | n/a |  | binary input | 1.0.66
PCS002.Sts.PAuto |  | n/a |  | binary input | 1.0.67 | Correct | Corrected
PCS002.Sts.QAuto |  | n/a |  | binary input | 1.0.68 | Correct
PCS002.Sts.Auto |  | n/a |  | binary input | 1.0.69
PCS003.Alm.Control |  | n/a |  | binary input | 1.0.70
PCS003.Alm.Derate |  | n/a |  | binary input | 1.0.71
PCS003.Alm.Cooling |  | n/a |  | binary input | 1.0.72
PCS003.Alm.Offline |  | n/a |  | binary input | 1.0.73
PCS003.Alm.Comm |  | n/a |  | binary input | 1.0.74
PCS003.Alm.EPO |  | n/a |  | binary input | 1.0.75
PCS003.Sts.CBMain |  | n/a |  | binary input | 1.0.76
PCS003.Sts.PAuto |  | n/a |  | binary input | 1.0.77 | Correct | Corrected
PCS003.Sts.QAuto |  | n/a |  | binary input | 1.0.78 | Correct | Corrected
PCS003.Sts.Auto |  | n/a |  | binary input | 1.0.79
PCS004.Alm.Control |  | n/a |  | binary input | 1.0.80
PCS004.Alm.Derate |  | n/a |  | binary input | 1.0.81
PCS004.Alm.Cooling |  | n/a |  | binary input | 1.0.82
PCS004.Alm.Offline |  | n/a |  | binary input | 1.0.83
PCS004.Alm.Comm |  | n/a |  | binary input | 1.0.84
PCS004.Alm.EPO |  | n/a |  | binary input | 1.0.85
PCS004.Sts.CBMain |  | n/a |  | binary input | 1.0.86
PCS004.Sts.PAuto |  | n/a |  | binary input | 1.0.87 | Correct | Corrected
PCS004.Sts.QAuto |  | n/a |  | binary input | 1.0.88 | Correct | Corrected
PCS004.Sts.Auto |  | n/a |  | binary input | 1.0.89
PCS005.Alm.Control |  | n/a |  | binary input | 1.0.90
PCS005.Alm.Derate |  | n/a |  | binary input | 1.0.91
PCS005.Alm.Cooling |  | n/a |  | binary input | 1.0.92
PCS005.Alm.Offline |  | n/a |  | binary input | 1.0.93
PCS005.Alm.Comm |  | n/a |  | binary input | 1.0.94
PCS005.Alm.EPO |  | n/a |  | binary input | 1.0.95
PCS005.Sts.CBMain |  | n/a |  | binary input | 1.0.96
PCS005.Sts.PAuto |  | n/a |  | binary input | 1.0.97 | Correct | Corrected
PCS005.Sts.QAuto |  | n/a |  | binary input | 1.0.98 | Correct | Corrected
PCS005.Sts.Auto |  | n/a |  | binary input | 1.0.99
PCS006.Alm.Control |  | n/a |  | binary input | 1.0.100
PCS006.Alm.Derate |  | n/a |  | binary input | 1.0.101
PCS006.Alm.Cooling |  | n/a |  | binary input | 1.0.102
PCS006.Alm.Offline |  | n/a |  | binary input | 1.0.103
PCS006.Alm.Comm |  | n/a |  | binary input | 1.0.104
PCS006.Alm.EPO |  | n/a |  | binary input | 1.0.105
PCS006.Sts.CBMain |  | n/a |  | binary input | 1.0.106
PCS006.Sts.PAuto |  | n/a |  | binary input | 1.0.107 | Correct | Corrected
PCS006.Sts.QAuto |  | n/a |  | binary input | 1.0.108 | Correct | Corrected
PCS006.Sts.Auto |  | n/a |  | binary input | 1.0.109
PCS007.Alm.Control |  | n/a |  | binary input | 1.0.110
PCS007.Alm.Derate |  | n/a |  | binary input | 1.0.111
PCS007.Alm.Cooling |  | n/a |  | binary input | 1.0.112
PCS007.Alm.Offline |  | n/a |  | binary input | 1.0.113
PCS007.Alm.Comm |  | n/a |  | binary input | 1.0.114
PCS007.Alm.EPO |  | n/a |  | binary input | 1.0.115
PCS007.Sts.CBMain |  | n/a |  | binary input | 1.0.116
PCS007.Sts.PAuto |  | n/a |  | binary input | 1.0.117 | Correct | Corrected
PCS007.Sts.QAuto |  | n/a |  | binary input | 1.0.118 | Correct | Corrected
PCS007.Sts.Auto |  | n/a |  | binary input | 1.0.119
PCS008.Alm.Control |  | n/a |  | binary input | 1.0.120
PCS008.Alm.Derate |  | n/a |  | binary input | 1.0.121
PCS008.Alm.Cooling |  | n/a |  | binary input | 1.0.122
PCS008.Alm.Offline |  | n/a |  | binary input | 1.0.123
PCS008.Alm.Comm |  | n/a |  | binary input | 1.0.124
PCS008.Alm.EPO |  | n/a |  | binary input | 1.0.125
PCS008.Sts.CBMain |  | n/a |  | binary input | 1.0.126
PCS008.Sts.PAuto |  | n/a |  | binary input | 1.0.127 | Correct | Corrected
PCS008.Sts.QAuto |  | n/a |  | binary input | 1.0.128 | Correct | Corrected
PCS008.Sts.Auto |  | n/a |  | binary input | 1.0.129
PCS009.Alm.Control |  | n/a |  | binary input | 1.0.130
PCS009.Alm.Derate |  | n/a |  | binary input | 1.0.131
PCS009.Alm.Cooling |  | n/a |  | binary input | 1.0.132
PCS009.Alm.Offline |  | n/a |  | binary input | 1.0.133
PCS009.Alm.Comm |  | n/a |  | binary input | 1.0.134
PCS009.Alm.EPO |  | n/a |  | binary input | 1.0.135
PCS009.Sts.CBMain |  | n/a |  | binary input | 1.0.136
PCS009.Sts.PAuto |  | n/a |  | binary input | 1.0.137 | Correct | Corrected
PCS009.Sts.QAuto |  | n/a |  | binary input | 1.0.138 | Correct | Corrected
PCS009.Sts.Auto |  | n/a |  | binary input | 1.0.139
PCS010.Alm.Control |  | n/a |  | binary input | 1.0.140
PCS010.Alm.Derate |  | n/a |  | binary input | 1.0.141
PCS010.Alm.Cooling |  | n/a |  | binary input | 1.0.142
PCS010.Alm.Offline |  | n/a |  | binary input | 1.0.143
PCS010.Alm.Comm |  | n/a |  | binary input | 1.0.144
PCS010.Alm.EPO |  | n/a |  | binary input | 1.0.145
PCS010.Sts.CBMain |  | n/a |  | binary input | 1.0.146
PCS010.Sts.PAuto |  | n/a |  | binary input | 1.0.147 | Correct | Corrected
PCS010.Sts.QAuto |  | n/a |  | binary input | 1.0.148 | Correct | Corrected
PCS010.Sts.Auto |  | n/a |  | binary input | 1.0.149
PCS011.Alm.Control |  | n/a |  | binary input | 1.0.150
PCS011.Alm.Derate |  | n/a |  | binary input | 1.0.151
PCS011.Alm.Cooling |  | n/a |  | binary input | 1.0.152
PCS011.Alm.Offline |  | n/a |  | binary input | 1.0.153
PCS011.Alm.Comm |  | n/a |  | binary input | 1.0.154
PCS011.Alm.EPO |  | n/a |  | binary input | 1.0.155
PCS011.Sts.CBMain |  | n/a |  | binary input | 1.0.156
PCS011.Sts.PAuto |  | n/a |  | binary input | 1.0.157 | Correct | Corrected
PCS011.Sts.QAuto |  | n/a |  | binary input | 1.0.158 | Correct | Corrected
PCS011.Sts.Auto |  | n/a |  | binary input | 1.0.159
PCS012.Alm.Control |  | n/a |  | binary input | 1.0.160
PCS012.Alm.Derate |  | n/a |  | binary input | 1.0.161
PCS012.Alm.Cooling |  | n/a |  | binary input | 1.0.162
PCS012.Alm.Offline |  | n/a |  | binary input | 1.0.163
PCS012.Alm.Comm |  | n/a |  | binary input | 1.0.164
PCS012.Alm.EPO |  | n/a |  | binary input | 1.0.165
PCS012.Sts.CBMain |  | n/a |  | binary input | 1.0.166
PCS012.Sts.PAuto |  | n/a |  | binary input | 1.0.167 | Correct | Corrected
PCS012.Sts.QAuto |  | n/a |  | binary input | 1.0.168 | Correct | Corrected
PCS012.Sts.Auto |  | n/a |  | binary input | 1.0.169
PCS013.Alm.Control |  | n/a |  | binary input | 1.0.170
PCS013.Alm.Derate |  | n/a |  | binary input | 1.0.171
PCS013.Alm.Cooling |  | n/a |  | binary input | 1.0.172
PCS013.Alm.Offline |  | n/a |  | binary input | 1.0.173
PCS013.Alm.Comm |  | n/a |  | binary input | 1.0.174
PCS013.Alm.EPO |  | n/a |  | binary input | 1.0.175
PCS013.Sts.CBMain |  | n/a |  | binary input | 1.0.176
PCS013.Sts.PAuto |  | n/a |  | binary input | 1.0.177 | Correct | Corrected
PCS013.Sts.QAuto |  | n/a |  | binary input | 1.0.178 | Correct | Corrected
PCS013.Sts.Auto |  | n/a |  | binary input | 1.0.179
PCS014.Alm.Control |  | n/a |  | binary input | 1.0.180
PCS014.Alm.Derate |  | n/a |  | binary input | 1.0.181
PCS014.Alm.Cooling |  | n/a |  | binary input | 1.0.182
PCS014.Alm.Offline |  | n/a |  | binary input | 1.0.183
PCS014.Alm.Comm |  | n/a |  | binary input | 1.0.184
PCS014.Alm.EPO |  | n/a |  | binary input | 1.0.185
PCS014.Sts.CBMain |  | n/a |  | binary input | 1.0.186
PCS014.Sts.PAuto |  | n/a |  | binary input | 1.0.187 | Correct
PCS014.Sts.QAuto |  | n/a |  | binary input | 1.0.188 | Correct | Corrected
PCS014.Sts.Auto |  | n/a |  | binary input | 1.0.189
PCS015.Alm.Control |  | n/a |  | binary input | 1.0.190
PCS015.Alm.Derate |  | n/a |  | binary input | 1.0.191
PCS015.Alm.Cooling |  | n/a |  | binary input | 1.0.192
PCS015.Alm.Offline |  | n/a |  | binary input | 1.0.193
PCS015.Alm.Comm |  | n/a |  | binary input | 1.0.194
PCS015.Alm.EPO |  | n/a |  | binary input | 1.0.195
PCS015.Sts.CBMain |  | n/a |  | binary input | 1.0.196
PCS015.Sts.PAuto |  | n/a |  | binary input | 1.0.197 | Correct
PCS015.Sts.QAuto |  | n/a |  | binary input | 1.0.198 | Correct | Corrected
PCS015.Sts.Auto |  | n/a |  | binary input | 1.0.199
PCS016.Alm.Control |  | n/a |  | binary input | 1.0.200
PCS016.Alm.Derate |  | n/a |  | binary input | 1.0.201
PCS016.Alm.Cooling |  | n/a |  | binary input | 1.0.202
PCS016.Alm.Offline |  | n/a |  | binary input | 1.0.203
PCS016.Alm.Comm |  | n/a |  | binary input | 1.0.204
PCS016.Alm.EPO |  | n/a |  | binary input | 1.0.205
PCS016.Sts.CBMain |  | n/a |  | binary input | 1.0.206
PCS016.Sts.PAuto |  | n/a |  | binary input | 1.0.207 | Correct
PCS016.Sts.QAuto |  | n/a |  | binary input | 1.0.208 | Correct
PCS016.Sts.Auto |  | n/a |  | binary input | 1.0.209
PCS017.Alm.Control |  | n/a |  | binary input | 1.0.210
PCS017.Alm.Derate |  | n/a |  | binary input | 1.0.211
PCS017.Alm.Cooling |  | n/a |  | binary input | 1.0.212
PCS017.Alm.Offline |  | n/a |  | binary input | 1.0.213
PCS017.Alm.Comm |  | n/a |  | binary input | 1.0.214
PCS017.Alm.EPO |  | n/a |  | binary input | 1.0.215
PCS017.Sts.CBMain |  | n/a |  | binary input | 1.0.216
PCS017.Sts.PAuto |  | n/a |  | binary input | 1.0.217 | Correct
PCS017.Sts.QAuto |  | n/a |  | binary input | 1.0.218 | Correct
PCS017.Sts.Auto |  | n/a |  | binary input | 1.0.219
PCS018.Alm.Control |  | n/a |  | binary input | 1.0.220
PCS018.Alm.Derate |  | n/a |  | binary input | 1.0.221
PCS018.Alm.Cooling |  | n/a |  | binary input | 1.0.222
PCS018.Alm.Offline |  | n/a |  | binary input | 1.0.223
PCS018.Alm.Comm |  | n/a |  | binary input | 1.0.224
PCS018.Alm.EPO |  | n/a |  | binary input | 1.0.225
PCS018.Sts.CBMain |  | n/a |  | binary input | 1.0.226
PCS018.Sts.PAuto |  | n/a |  | binary input | 1.0.227 | Correct | Corrected
PCS018.Sts.QAuto |  | n/a |  | binary input | 1.0.228 | Correct
PCS018.Sts.Auto |  | n/a |  | binary input | 1.0.229
PCS019.Alm.Control |  | n/a |  | binary input | 1.0.230
PCS019.Alm.Derate |  | n/a |  | binary input | 1.0.231
PCS019.Alm.Cooling |  | n/a |  | binary input | 1.0.232
PCS019.Alm.Offline |  | n/a |  | binary input | 1.0.233
PCS019.Alm.Comm |  | n/a |  | binary input | 1.0.234
PCS019.Alm.EPO |  | n/a |  | binary input | 1.0.235
PCS019.Sts.CBMain |  | n/a |  | binary input | 1.0.236
PCS019.Sts.PAuto |  | n/a |  | binary input | 1.0.237 | Correct | Corrected
PCS019.Sts.QAuto |  | n/a |  | binary input | 1.0.238 | Correct
PCS019.Sts.Auto |  | n/a |  | binary input | 1.0.239
PCS020.Alm.Control |  | n/a |  | binary input | 1.0.240
PCS020.Alm.Derate |  | n/a |  | binary input | 1.0.241
PCS020.Alm.Cooling |  | n/a |  | binary input | 1.0.242
PCS020.Alm.Offline |  | n/a |  | binary input | 1.0.243
PCS020.Alm.Comm |  | n/a |  | binary input | 1.0.244
PCS020.Alm.EPO |  | n/a |  | binary input | 1.0.245
PCS020.Sts.CBMain |  | n/a |  | binary input | 1.0.246
PCS020.Sts.PAuto |  | n/a |  | binary input | 1.0.247 | Correct | Corrected
PCS020.Sts.QAuto |  | n/a |  | binary input | 1.0.248 | Correct | Corrected
PCS020.Sts.Auto |  | n/a |  | binary input | 1.0.249
PCS021.Alm.Control |  | n/a |  | binary input | 1.0.250
PCS021.Alm.Derate |  | n/a |  | binary input | 1.0.251
PCS021.Alm.Cooling |  | n/a |  | binary input | 1.0.252
PCS021.Alm.Offline |  | n/a |  | binary input | 1.0.253
PCS021.Alm.Comm |  | n/a |  | binary input | 1.0.254
PCS021.Alm.EPO |  | n/a |  | binary input | 1.0.255
PCS021.Sts.CBMain |  | n/a |  | binary input | 1.0.256
PCS021.Sts.PAuto |  | n/a |  | binary input | 1.0.257 | Correct | Corrected
PCS021.Sts.QAuto |  | n/a |  | binary input | 1.0.258 | Correct | Corrected
PCS021.Sts.Auto |  | n/a |  | binary input | 1.0.259
PCS022.Alm.Control |  | n/a |  | binary input | 1.0.260
PCS022.Alm.Derate |  | n/a |  | binary input | 1.0.261
PCS022.Alm.Cooling |  | n/a |  | binary input | 1.0.262
PCS022.Alm.Offline |  | n/a |  | binary input | 1.0.263
PCS022.Alm.Comm |  | n/a |  | binary input | 1.0.264
PCS022.Alm.EPO |  | n/a |  | binary input | 1.0.265
PCS022.Sts.CBMain |  | n/a |  | binary input | 1.0.266
PCS022.Sts.PAuto |  | n/a |  | binary input | 1.0.267 | Correct | Corrected
PCS022.Sts.QAuto |  | n/a |  | binary input | 1.0.268 | Correct | Corrected
PCS022.Sts.Auto |  | n/a |  | binary input | 1.0.269
PCS023.Alm.Control |  | n/a |  | binary input | 1.0.270
PCS023.Alm.Derate |  | n/a |  | binary input | 1.0.271
PCS023.Alm.Cooling |  | n/a |  | binary input | 1.0.272
PCS023.Alm.Offline |  | n/a |  | binary input | 1.0.273
PCS023.Alm.Comm |  | n/a |  | binary input | 1.0.274
PCS023.Alm.EPO |  | n/a |  | binary input | 1.0.275
PCS023.Sts.CBMain |  | n/a |  | binary input | 1.0.276
PCS023.Sts.PAuto |  | n/a |  | binary input | 1.0.277 | Correct | Corrected
PCS023.Sts.QAuto |  | n/a |  | binary input | 1.0.278 | Correct | Corrected
PCS023.Sts.Auto |  | n/a |  | binary input | 1.0.279
Note on A82: Alberto Pesce: tag: PPC..Sts.ControlMode Changed to PPC..Sts.QControlMode

## Revision History
Author | Comments | Date
Column1 | Column3 | Column5
NJM | Intial Draft | 2017-11-02
NJM | Rev 2 - Added met station and inverter kWh delivered tags | 2017-12-13
PES | Rev 3 - Tag PPC..Sts.ControlMode changed to PPC..Sts.QControlMode and GREEN tags set as available throught DNP3, YELLOW tags not available now | 2017-12-15