## Sheet1
Message Structure
Message Type: | DNP 3.0 TCP/IP | Originating Device: | FS RTU | Destination Device: | SYS600 (MicroSCADA)
Port: | 20000 | Originating IP: | unknown | Destination IP: | 192.168.1.31
|  | Originating Subnet: | unknown | Destination Subnet: | 255.255.255.0
|  | Originating Gateway: | unknown | Destination Gateway: | unknown
|  | Originating ID: | 1 | Destination ID: | 100 (Slave Address)
[Eng Unit]
LN | IX | CX | OI | OX | ST | DNP3 Address
SYS_A0001I | 10 |  | NCC 1 APL 1 | Status of Application state |  | 30.5.1
SYS_A0001I | 20 |  | NCC 1 APL 1 | Status of Application HSB state |  | 30.5.2
SYS_N0003I | 21 |  | NCC 1 Line 1 | Status of line 1 (Node 3) |  | 30.5.3
SYS_N0003I | 121 |  | NCC 1 Line 1 | Status of line 1 (Node 3) |  | 30.5.4
SYS_N0003I | 30 |  | NCC 1 Line 10 | Status of line 10 (Node 3) |  | 30.5.5
SYS_N0003I | 130 |  | NCC 1 Line 10 | Status of line 10 (Node 3) |  | 30.5.6
SYS_N0003I | 31 |  | NCC 1 Line 11 | Status of line 11 (Node 3) |  | 30.5.7
SYS_N0003I | 131 |  | NCC 1 Line 11 | Status of line 11 (Node 3) |  | 30.5.8
SYS_N0003I | 22 |  | NCC 1 Line 2 | Status of line 2 (Node 3) |  | 30.5.9
SYS_N0003I | 122 |  | NCC 1 Line 2 | Status of line 2 (Node 3) |  | 30.5.10
SYS_N0003I | 23 |  | NCC 1 Line 3 | Status of line 3 (Node 3) |  | 30.5.11
SYS_N0003I | 123 |  | NCC 1 Line 3 | Status of line 3 (Node 3) |  | 30.5.12
SYS_N0003I | 24 |  | NCC 1 Line 4 | Status of line 4 (Node 3) |  | 30.5.13
SYS_N0003I | 124 |  | NCC 1 Line 4 | Status of line 4 (Node 3) |  | 30.5.14
SYS_N0003I | 25 |  | NCC 1 Line 5 | Status of line 5 (Node 3) |  | 30.5.15
SYS_N0003I | 125 |  | NCC 1 Line 5 | Status of line 5 (Node 3) |  | 30.5.16
SYS_N0003I | 26 |  | NCC 1 Line 6 | Status of line 6 (Node 3) |  | 30.5.17
SYS_N0003I | 126 |  | NCC 1 Line 6 | Status of line 6 (Node 3) |  | 30.5.18
SYS_N0003I | 27 |  | NCC 1 Line 7 | Status of line 7 (Node 3) |  | 30.5.19
SYS_N0003I | 127 |  | NCC 1 Line 7 | Status of line 7 (Node 3) |  | 30.5.20
SYS_N0003I | 28 |  | NCC 1 Line 8 | Status of line 8 (Node 3) |  | 30.5.21
SYS_N0003I | 128 |  | NCC 1 Line 8 | Status of line 8 (Node 3) |  | 30.5.22
SYS_N0003I | 29 |  | NCC 1 Line 9 | Status of line 9 (Node 3) |  | 30.5.23
SYS_N0003I | 129 |  | NCC 1 Line 9 | Status of line 9 (Node 3) |  | 30.5.24
SYS_N0003I | 10 |  | NCC 1 NET 3 | Status of NET 3 |  | 30.5.25
SYS_N0005I | 10 |  | NCC 1 NET 5 | Status of NET 5 |  | 30.5.26
SYS_N0005I | 110 |  | NCC 1 NET 5 | Status of NET 5 |  | 30.5.27
SYS_S0001I | 10 |  | NCC 1 Station 1 | Status of station 1 |  | 30.5.28
SYS_S0001I | 110 |  | NCC 1 Station 1 | Status of station 1 |  | 30.5.29
SYS_S0010I | 10 |  | NCC 1 Station 10 | Status of station 10 |  | 30.5.30
SYS_S0010I | 110 |  | NCC 1 Station 10 | Status of station 10 |  | 30.5.31
SYS_S1003I | 10 |  | NCC 1 Station 1003 | Status of station 1003 |  | 30.5.32
SYS_S1003I | 110 |  | NCC 1 Station 1003 | Status of station 1003 |  | 30.5.33
SYS_S0103I | 10 |  | NCC 1 Station 103 | Status of station 103 |  | 30.5.34
SYS_S0103I | 110 |  | NCC 1 Station 103 | Status of station 103 |  | 30.5.35
SYS_S1032I | 10 |  | NCC 1 Station 1032 | Status of station 1032 |  | 30.5.36
SYS_S1032I | 110 |  | NCC 1 Station 1032 | Status of station 1032 |  | 30.5.37
SYS_S1033I | 10 |  | NCC 1 Station 1033 | Status of station 1033 |  | 30.5.38
SYS_S1033I | 110 |  | NCC 1 Station 1033 | Status of station 1033 |  | 30.5.39
SYS_S0011I | 10 |  | NCC 1 Station 11 | Status of station 11 |  | 30.5.40
SYS_S0011I | 110 |  | NCC 1 Station 11 | Status of station 11 |  | 30.5.41
SYS_S1103I | 10 |  | NCC 1 Station 1103 | Status of station 1103 |  | 30.5.42
SYS_S1103I | 110 |  | NCC 1 Station 1103 | Status of station 1103 |  | 30.5.43
SYS_S1132I | 10 |  | NCC 1 Station 1132 | Status of station 1132 |  | 30.5.44
SYS_S1132I | 110 |  | NCC 1 Station 1132 | Status of station 1132 |  | 30.5.45
SYS_S1133I | 10 |  | NCC 1 Station 1133 | Status of station 1133 |  | 30.5.46
SYS_S1133I | 110 |  | NCC 1 Station 1133 | Status of station 1133 |  | 30.5.47
SYS_S0012I | 10 |  | NCC 1 Station 12 | Status of station 12 |  | 30.5.48
SYS_S0012I | 110 |  | NCC 1 Station 12 | Status of station 12 |  | 30.5.49
SYS_S1203I | 10 |  | NCC 1 Station 1203 | Status of station 1203 |  | 30.5.50
SYS_S1203I | 110 |  | NCC 1 Station 1203 | Status of station 1203 |  | 30.5.51
SYS_S1232I | 10 |  | NCC 1 Station 1232 | Status of station 1232 |  | 30.5.52
SYS_S1232I | 110 |  | NCC 1 Station 1232 | Status of station 1232 |  | 30.5.53
SYS_S1233I | 10 |  | NCC 1 Station 1233 | Status of station 1233 |  | 30.5.54
SYS_S1233I | 110 |  | NCC 1 Station 1233 | Status of station 1233 |  | 30.5.55
SYS_S0013I | 10 |  | NCC 1 Station 13 | Status of station 13 |  | 30.5.56
SYS_S0013I | 110 |  | NCC 1 Station 13 | Status of station 13 |  | 30.5.57
SYS_S1303I | 10 |  | NCC 1 Station 1303 | Status of station 1303 |  | 30.5.58
SYS_S1303I | 110 |  | NCC 1 Station 1303 | Status of station 1303 |  | 30.5.59
SYS_S0132I | 10 |  | NCC 1 Station 132 | Status of station 132 |  | 30.5.60
SYS_S0132I | 110 |  | NCC 1 Station 132 | Status of station 132 |  | 30.5.61
SYS_S0133I | 10 |  | NCC 1 Station 133 | Status of station 133 |  | 30.5.62
SYS_S0133I | 110 |  | NCC 1 Station 133 | Status of station 133 |  | 30.5.63
SYS_S1332I | 10 |  | NCC 1 Station 1332 | Status of station 1332 |  | 30.5.64
SYS_S1332I | 110 |  | NCC 1 Station 1332 | Status of station 1332 |  | 30.5.65
SYS_S1333I | 10 |  | NCC 1 Station 1333 | Status of station 1333 |  | 30.5.66
SYS_S1333I | 110 |  | NCC 1 Station 1333 | Status of station 1333 |  | 30.5.67
SYS_S0014I | 10 |  | NCC 1 Station 14 | Status of station 14 |  | 30.5.68
SYS_S0014I | 110 |  | NCC 1 Station 14 | Status of station 14 |  | 30.5.69
SYS_S1403I | 10 |  | NCC 1 Station 1403 | Status of station 1403 |  | 30.5.70
SYS_S1403I | 110 |  | NCC 1 Station 1403 | Status of station 1403 |  | 30.5.71
SYS_S1432I | 10 |  | NCC 1 Station 1432 | Status of station 1432 |  | 30.5.72
SYS_S1432I | 110 |  | NCC 1 Station 1432 | Status of station 1432 |  | 30.5.73
SYS_S1433I | 10 |  | NCC 1 Station 1433 | Status of station 1433 |  | 30.5.74
SYS_S1433I | 110 |  | NCC 1 Station 1433 | Status of station 1433 |  | 30.5.75
SYS_S0015I | 10 |  | NCC 1 Station 15 | Status of station 15 |  | 30.5.76
SYS_S0015I | 110 |  | NCC 1 Station 15 | Status of station 15 |  | 30.5.77
SYS_S1503I | 10 |  | NCC 1 Station 1503 | Status of station 1503 |  | 30.5.78
SYS_S1503I | 110 |  | NCC 1 Station 1503 | Status of station 1503 |  | 30.5.79
SYS_S1532I | 10 |  | NCC 1 Station 1532 | Status of station 1532 |  | 30.5.80
SYS_S1532I | 110 |  | NCC 1 Station 1532 | Status of station 1532 |  | 30.5.81
SYS_S1533I | 10 |  | NCC 1 Station 1533 | Status of station 1533 |  | 30.5.82
SYS_S1533I | 110 |  | NCC 1 Station 1533 | Status of station 1533 |  | 30.5.83
SYS_S0016I | 10 |  | NCC 1 Station 16 | Status of station 16 |  | 30.5.84
SYS_S0016I | 110 |  | NCC 1 Station 16 | Status of station 16 |  | 30.5.85
SYS_S0160I | 10 |  | NCC 1 Station 160 | Status of station 160 |  | 30.5.86
SYS_S0160I | 110 |  | NCC 1 Station 160 | Status of station 160 |  | 30.5.87
SYS_S1603I | 10 |  | NCC 1 Station 1603 | Status of station 1603 |  | 30.5.88
SYS_S1603I | 110 |  | NCC 1 Station 1603 | Status of station 1603 |  | 30.5.89
SYS_S0161I | 10 |  | NCC 1 Station 161 | Status of station 161 |  | 30.5.90
SYS_S0161I | 110 |  | NCC 1 Station 161 | Status of station 161 |  | 30.5.91
SYS_S0163I | 10 |  | NCC 1 Station 163 | Status of station 163 |  | 30.5.92
SYS_S0163I | 110 |  | NCC 1 Station 163 | Status of station 163 |  | 30.5.93
SYS_S1632I | 10 |  | NCC 1 Station 1632 | Status of station 1632 |  | 30.5.94
SYS_S1632I | 110 |  | NCC 1 Station 1632 | Status of station 1632 |  | 30.5.95
SYS_S1633I | 10 |  | NCC 1 Station 1633 | Status of station 1633 |  | 30.5.96
SYS_S1633I | 110 |  | NCC 1 Station 1633 | Status of station 1633 |  | 30.5.97
SYS_S0017I | 10 |  | NCC 1 Station 17 | Status of station 17 |  | 30.5.98
SYS_S0017I | 110 |  | NCC 1 Station 17 | Status of station 17 |  | 30.5.99
SYS_S1703I | 10 |  | NCC 1 Station 1703 | Status of station 1703 |  | 30.5.100
SYS_S1703I | 110 |  | NCC 1 Station 1703 | Status of station 1703 |  | 30.5.101
SYS_S1732I | 10 |  | NCC 1 Station 1732 | Status of station 1732 |  | 30.5.102
SYS_S1732I | 110 |  | NCC 1 Station 1732 | Status of station 1732 |  | 30.5.103
SYS_S1733I | 10 |  | NCC 1 Station 1733 | Status of station 1733 |  | 30.5.104
SYS_S1733I | 110 |  | NCC 1 Station 1733 | Status of station 1733 |  | 30.5.105
SYS_S0018I | 10 |  | NCC 1 Station 18 | Status of station 18 |  | 30.5.106
SYS_S0018I | 110 |  | NCC 1 Station 18 | Status of station 18 |  | 30.5.107
SYS_S1803I | 10 |  | NCC 1 Station 1803 | Status of station 1803 |  | 30.5.108
SYS_S1803I | 110 |  | NCC 1 Station 1803 | Status of station 1803 |  | 30.5.109
SYS_S1832I | 10 |  | NCC 1 Station 1832 | Status of station 1832 |  | 30.5.110
SYS_S1832I | 110 |  | NCC 1 Station 1832 | Status of station 1832 |  | 30.5.111
SYS_S1833I | 10 |  | NCC 1 Station 1833 | Status of station 1833 |  | 30.5.112
SYS_S1833I | 110 |  | NCC 1 Station 1833 | Status of station 1833 |  | 30.5.113
SYS_S0019I | 10 |  | NCC 1 Station 19 | Status of station 19 |  | 30.5.114
SYS_S0019I | 110 |  | NCC 1 Station 19 | Status of station 19 |  | 30.5.115
SYS_S1903I | 10 |  | NCC 1 Station 1903 | Status of station 1903 |  | 30.5.116
SYS_S1903I | 110 |  | NCC 1 Station 1903 | Status of station 1903 |  | 30.5.117
SYS_S1932I | 10 |  | NCC 1 Station 1932 | Status of station 1932 |  | 30.5.118
SYS_S1932I | 110 |  | NCC 1 Station 1932 | Status of station 1932 |  | 30.5.119
SYS_S1933I | 10 |  | NCC 1 Station 1933 | Status of station 1933 |  | 30.5.120
SYS_S1933I | 110 |  | NCC 1 Station 1933 | Status of station 1933 |  | 30.5.121
SYS_S0002I | 10 |  | NCC 1 Station 2 | Status of station 2 |  | 30.5.122
SYS_S0002I | 110 |  | NCC 1 Station 2 | Status of station 2 |  | 30.5.123
SYS_S0020I | 10 |  | NCC 1 Station 20 | Status of station 20 |  | 30.5.124
SYS_S0020I | 110 |  | NCC 1 Station 20 | Status of station 20 |  | 30.5.125
SYS_S2003I | 10 |  | NCC 1 Station 2003 | Status of station 2003 |  | 30.5.126
SYS_S2003I | 110 |  | NCC 1 Station 2003 | Status of station 2003 |  | 30.5.127
SYS_S0201I | 10 |  | NCC 1 Station 201 | Status of station 201 |  | 30.5.128
SYS_S0201I | 110 |  | NCC 1 Station 201 | Status of station 201 |  | 30.5.129
SYS_S0203I | 10 |  | NCC 1 Station 203 | Status of station 203 |  | 30.5.130
SYS_S0203I | 110 |  | NCC 1 Station 203 | Status of station 203 |  | 30.5.131
SYS_S2032I | 10 |  | NCC 1 Station 2032 | Status of station 2032 |  | 30.5.132
SYS_S2032I | 110 |  | NCC 1 Station 2032 | Status of station 2032 |  | 30.5.133
SYS_S2033I | 10 |  | NCC 1 Station 2033 | Status of station 2033 |  | 30.5.134
SYS_S2033I | 110 |  | NCC 1 Station 2033 | Status of station 2033 |  | 30.5.135
SYS_S0021I | 10 |  | NCC 1 Station 21 | Status of station 21 |  | 30.5.136
SYS_S0021I | 110 |  | NCC 1 Station 21 | Status of station 21 |  | 30.5.137
SYS_S2103I | 10 |  | NCC 1 Station 2103 | Status of station 2103 |  | 30.5.138
SYS_S2103I | 110 |  | NCC 1 Station 2103 | Status of station 2103 |  | 30.5.139
SYS_S2132I | 10 |  | NCC 1 Station 2132 | Status of station 2132 |  | 30.5.140
SYS_S2132I | 110 |  | NCC 1 Station 2132 | Status of station 2132 |  | 30.5.141
SYS_S2133I | 10 |  | NCC 1 Station 2133 | Status of station 2133 |  | 30.5.142
SYS_S2133I | 110 |  | NCC 1 Station 2133 | Status of station 2133 |  | 30.5.143
SYS_S0022I | 10 |  | NCC 1 Station 22 | Status of station 22 |  | 30.5.144
SYS_S0022I | 110 |  | NCC 1 Station 22 | Status of station 22 |  | 30.5.145
SYS_S2203I | 10 |  | NCC 1 Station 2203 | Status of station 2203 |  | 30.5.146
SYS_S2203I | 110 |  | NCC 1 Station 2203 | Status of station 2203 |  | 30.5.147
SYS_S2232I | 10 |  | NCC 1 Station 2232 | Status of station 2232 |  | 30.5.148
SYS_S2232I | 110 |  | NCC 1 Station 2232 | Status of station 2232 |  | 30.5.149
SYS_S2233I | 10 |  | NCC 1 Station 2233 | Status of station 2233 |  | 30.5.150
SYS_S2233I | 110 |  | NCC 1 Station 2233 | Status of station 2233 |  | 30.5.151
SYS_S0023I | 10 |  | NCC 1 Station 23 | Status of station 23 |  | 30.5.152
SYS_S0023I | 110 |  | NCC 1 Station 23 | Status of station 23 |  | 30.5.153
SYS_S2303I | 10 |  | NCC 1 Station 2303 | Status of station 2303 |  | 30.5.154
SYS_S2303I | 110 |  | NCC 1 Station 2303 | Status of station 2303 |  | 30.5.155
SYS_S0232I | 10 |  | NCC 1 Station 232 | Status of station 232 |  | 30.5.156
SYS_S0232I | 110 |  | NCC 1 Station 232 | Status of station 232 |  | 30.5.157
SYS_S0233I | 10 |  | NCC 1 Station 233 | Status of station 233 |  | 30.5.158
SYS_S0233I | 110 |  | NCC 1 Station 233 | Status of station 233 |  | 30.5.159
SYS_S2332I | 10 |  | NCC 1 Station 2332 | Status of station 2332 |  | 30.5.160
SYS_S2332I | 110 |  | NCC 1 Station 2332 | Status of station 2332 |  | 30.5.161
SYS_S2333I | 10 |  | NCC 1 Station 2333 | Status of station 2333 |  | 30.5.162
SYS_S2333I | 110 |  | NCC 1 Station 2333 | Status of station 2333 |  | 30.5.163
SYS_S0260I | 10 |  | NCC 1 Station 260 | Status of station 260 |  | 30.5.164
SYS_S0260I | 110 |  | NCC 1 Station 260 | Status of station 260 |  | 30.5.165
SYS_S0261I | 10 |  | NCC 1 Station 261 | Status of station 261 |  | 30.5.166
SYS_S0261I | 110 |  | NCC 1 Station 261 | Status of station 261 |  | 30.5.167
SYS_S0263I | 10 |  | NCC 1 Station 263 | Status of station 263 |  | 30.5.168
SYS_S0263I | 110 |  | NCC 1 Station 263 | Status of station 263 |  | 30.5.169
SYS_S0003I | 10 |  | NCC 1 Station 3 | Status of station 3 |  | 30.5.170
SYS_S0003I | 110 |  | NCC 1 Station 3 | Status of station 3 |  | 30.5.171
SYS_S0303I | 10 |  | NCC 1 Station 303 | Status of station 303 |  | 30.5.172
SYS_S0303I | 110 |  | NCC 1 Station 303 | Status of station 303 |  | 30.5.173
SYS_S0031I | 10 |  | NCC 1 Station 31 | Status of station 31 |  | 30.5.174
SYS_S0031I | 110 |  | NCC 1 Station 31 | Status of station 31 |  | 30.5.175
SYS_S0332I | 10 |  | NCC 1 Station 332 | Status of station 332 |  | 30.5.176
SYS_S0332I | 110 |  | NCC 1 Station 332 | Status of station 332 |  | 30.5.177
SYS_S0333I | 10 |  | NCC 1 Station 333 | Status of station 333 |  | 30.5.178
SYS_S0333I | 110 |  | NCC 1 Station 333 | Status of station 333 |  | 30.5.179
SYS_S0360I | 10 |  | NCC 1 Station 360 | Status of station 360 |  | 30.5.180
SYS_S0360I | 110 |  | NCC 1 Station 360 | Status of station 360 |  | 30.5.181
SYS_S0361I | 10 |  | NCC 1 Station 361 | Status of station 361 |  | 30.5.182
SYS_S0361I | 110 |  | NCC 1 Station 361 | Status of station 361 |  | 30.5.183
SYS_S0363I | 10 |  | NCC 1 Station 363 | Status of station 363 |  | 30.5.184
SYS_S0363I | 110 |  | NCC 1 Station 363 | Status of station 363 |  | 30.5.185
SYS_S0004I | 10 |  | NCC 1 Station 4 | Status of station 4 |  | 30.5.186
SYS_S0004I | 110 |  | NCC 1 Station 4 | Status of station 4 |  | 30.5.187
SYS_S0403I | 10 |  | NCC 1 Station 403 | Status of station 403 |  | 30.5.188
SYS_S0403I | 110 |  | NCC 1 Station 403 | Status of station 403 |  | 30.5.189
SYS_S0432I | 10 |  | NCC 1 Station 432 | Status of station 432 |  | 30.5.190
SYS_S0432I | 110 |  | NCC 1 Station 432 | Status of station 432 |  | 30.5.191
SYS_S0433I | 10 |  | NCC 1 Station 433 | Status of station 433 |  | 30.5.192
SYS_S0433I | 110 |  | NCC 1 Station 433 | Status of station 433 |  | 30.5.193
SYS_S0460I | 10 |  | NCC 1 Station 460 | Status of station 460 |  | 30.5.194
SYS_S0460I | 110 |  | NCC 1 Station 460 | Status of station 460 |  | 30.5.195
SYS_S0461I | 10 |  | NCC 1 Station 461 | Status of station 461 |  | 30.5.196
SYS_S0461I | 110 |  | NCC 1 Station 461 | Status of station 461 |  | 30.5.197
SYS_S0463I | 10 |  | NCC 1 Station 463 | Status of station 463 |  | 30.5.198
SYS_S0463I | 110 |  | NCC 1 Station 463 | Status of station 463 |  | 30.5.199
SYS_S0005I | 10 |  | NCC 1 Station 5 | Status of station 5 |  | 30.5.200
SYS_S0005I | 110 |  | NCC 1 Station 5 | Status of station 5 |  | 30.5.201
SYS_S0503I | 10 |  | NCC 1 Station 503 | Status of station 503 |  | 30.5.202
SYS_S0503I | 110 |  | NCC 1 Station 503 | Status of station 503 |  | 30.5.203
SYS_S0051I | 10 |  | NCC 1 Station 51 | Status of station 51 |  | 30.5.204
SYS_S0051I | 110 |  | NCC 1 Station 51 | Status of station 51 |  | 30.5.205
SYS_S0532I | 10 |  | NCC 1 Station 532 | Status of station 532 |  | 30.5.206
SYS_S0532I | 110 |  | NCC 1 Station 532 | Status of station 532 |  | 30.5.207
SYS_S0533I | 10 |  | NCC 1 Station 533 | Status of station 533 |  | 30.5.208
SYS_S0533I | 110 |  | NCC 1 Station 533 | Status of station 533 |  | 30.5.209
SYS_S0006I | 10 |  | NCC 1 Station 6 | Status of station 6 |  | 30.5.210
SYS_S0006I | 110 |  | NCC 1 Station 6 | Status of station 6 |  | 30.5.211
SYS_S0603I | 10 |  | NCC 1 Station 603 | Status of station 603 |  | 30.5.212
SYS_S0603I | 110 |  | NCC 1 Station 603 | Status of station 603 |  | 30.5.213
SYS_S0632I | 10 |  | NCC 1 Station 632 | Status of station 632 |  | 30.5.214
SYS_S0632I | 110 |  | NCC 1 Station 632 | Status of station 632 |  | 30.5.215
SYS_S0633I | 10 |  | NCC 1 Station 633 | Status of station 633 |  | 30.5.216
SYS_S0633I | 110 |  | NCC 1 Station 633 | Status of station 633 |  | 30.5.217
SYS_S0007I | 10 |  | NCC 1 Station 7 | Status of station 7 |  | 30.5.218
SYS_S0007I | 110 |  | NCC 1 Station 7 | Status of station 7 |  | 30.5.219
SYS_S0703I | 10 |  | NCC 1 Station 703 | Status of station 703 |  | 30.5.220
SYS_S0703I | 110 |  | NCC 1 Station 703 | Status of station 703 |  | 30.5.221
SYS_S0732I | 10 |  | NCC 1 Station 732 | Status of station 732 |  | 30.5.222
SYS_S0732I | 110 |  | NCC 1 Station 732 | Status of station 732 |  | 30.5.223
SYS_S0733I | 10 |  | NCC 1 Station 733 | Status of station 733 |  | 30.5.224
SYS_S0733I | 110 |  | NCC 1 Station 733 | Status of station 733 |  | 30.5.225
SYS_S0008I | 10 |  | NCC 1 Station 8 | Status of station 8 |  | 30.5.226
SYS_S0008I | 110 |  | NCC 1 Station 8 | Status of station 8 |  | 30.5.227
SYS_S0803I | 10 |  | NCC 1 Station 803 | Status of station 803 |  | 30.5.228
SYS_S0803I | 110 |  | NCC 1 Station 803 | Status of station 803 |  | 30.5.229
SYS_S0832I | 10 |  | NCC 1 Station 832 | Status of station 832 |  | 30.5.230
SYS_S0832I | 110 |  | NCC 1 Station 832 | Status of station 832 |  | 30.5.231
SYS_S0833I | 10 |  | NCC 1 Station 833 | Status of station 833 |  | 30.5.232
SYS_S0833I | 110 |  | NCC 1 Station 833 | Status of station 833 |  | 30.5.233
SYS_S0009I | 10 |  | NCC 1 Station 9 | Status of station 9 |  | 30.5.234
SYS_S0009I | 110 |  | NCC 1 Station 9 | Status of station 9 |  | 30.5.235
SYS_S0903I | 10 |  | NCC 1 Station 903 | Status of station 903 |  | 30.5.236
SYS_S0903I | 110 |  | NCC 1 Station 903 | Status of station 903 |  | 30.5.237
SYS_S0932I | 10 |  | NCC 1 Station 932 | Status of station 932 |  | 30.5.238
SYS_S0932I | 110 |  | NCC 1 Station 932 | Status of station 932 |  | 30.5.239
SYS_S0933I | 10 |  | NCC 1 Station 933 | Status of station 933 |  | 30.5.240
SYS_S0933I | 110 |  | NCC 1 Station 933 | Status of station 933 |  | 30.5.241
SUCAPBLR | 20 |  | SU CAP | Bay blockings | Blocking | 30.5.242
SUCAPBLR | 21 |  | SU CAP | Bay selection on monitor | Sessions | 30.5.243
SUCAP1BR | 15 |  | SU CAP1 BR | Breaker device control block | Blocking | 30.5.244
SUCAP1BR | 18 |  | SU CAP1 BR | Cause of interlocking | Cause | 30.5.245
SUCAP1BR | 19 |  | SU CAP1 BR | Breaker selection on monitor | Sessions | 30.5.246
SUCAP1BR | 55 |  | SU CAP1 BR | Add cause of command | Add Cause | 30.5.247
SUCAP2BR | 15 |  | SU CAP2 BR | Breaker device control block | Blocking | 30.5.248
SUCAP2BR | 18 |  | SU CAP2 BR | Cause of interlocking | Cause | 30.5.249
SUCAP2BR | 19 |  | SU CAP2 BR | Breaker selection on monitor | Sessions | 30.5.250
SUCAP2BR | 55 |  | SU CAP2 BR | Add cause of command | Add Cause | 30.5.251
SUF152F1 | 15 |  | SU F1 52F1 | Breaker device control block | Blocking | 30.5.252
SUF152F1 | 18 |  | SU F1 52F1 | Cause of interlocking | Cause | 30.5.253
SUF152F1 | 19 |  | SU F1 52F1 | Breaker selection on monitor | Sessions | 30.5.254
SUF152F1 | 55 |  | SU F1 52F1 | Add cause of command | Add Cause | 30.5.255
SUF152I | 131 |  | SU F1 52M | Current | A | 30.5.256
SUF152P | 133 |  | SU F1 52M | Active Power | MW | 30.5.257
SUF152P | 134 |  | SU F1 52M | Reactive Power | Mvar | 30.5.258
SUF152PF | 136 |  | SU F1 52M | Power Factor | Cosfii | 30.5.259
SUF152V | 132 |  | SU F1 52M | Voltage | kV | 30.5.260
SUF1 | 20 |  | SU F1 BAY | Bay blockings | Blocking | 30.5.261
SUF1 | 21 |  | SU F1 BAY | Bay selection on monitor | Sessions | 30.5.262
SUF1INV1 | 1 | DC voltage DC plus to DC minus | SU F1 INV1 | DcMs_Vol | V | 30.5.263
SUF1INV1 | 2 | DC current inverter bridge 1 | SU F1 INV1 | DcMs_Amp_Stk1 | A | 30.5.264
SUF1INV1 | 3 | DC current inverter bridge 2 | SU F1 INV1 | DcMs_Amp_Stk2 | A | 30.5.265
SUF1INV1 | 4 | DC current inverter bridge 3 | SU F1 INV1 | DcMs_Amp_Stk3 | A | 30.5.266
SUF1INV1 | 5 | DC current, total | SU F1 INV1 | DcMs_TotAmp | A | 30.5.267
SUF1INV1 | 6 | DC power, total | SU F1 INV1 | DcMs_TotWatt | kW | 30.5.268
SUF1INV1 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV1 | InvMs_DclVol_Stk1 | V | 30.5.269
SUF1INV1 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV1 | InvMs_DclVol_Stk2 | V | 30.5.270
SUF1INV1 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV1 | InvMs_DclVol_Stk3 | V | 30.5.271
SUF1INV1 | 10 | AC current L1, total | SU F1 INV1 | InvMs_TotA_PhsA | A | 30.5.272
SUF1INV1 | 11 | AC current L2, total | SU F1 INV1 | InvMs_TotA_PhsB | A | 30.5.273
SUF1INV1 | 12 | AC current L3, total | SU F1 INV1 | InvMs_TotA_PhsC | A | 30.5.274
SUF1INV1 | 13 | Power factor (cos phi) | SU F1 INV1 | InvMs_PF | "-" | 30.5.275
SUF1INV1 | 14 | Apparent power, total | SU F1 INV1 | InvMs_TotVA | kVA | 30.5.276
SUF1INV1 | 15 | Active power, total | SU F1 INV1 | InvMs_TotW | kW | 30.5.277
SUF1INV1 | 16 | Reactive power, total | SU F1 INV1 | InvMs_TotVAr | kVAr | 30.5.278
SUF1INV1 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV1 | GriMs_V_PhsAB | V | 30.5.279
SUF1INV1 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV1 | GriMs_V_PhsBC | V | 30.5.280
SUF1INV1 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV1 | GriMs_V_PhsCA | V | 30.5.281
SUF1INV1 | 20 | Power frequency | SU F1 INV1 | GriMs_Hz | Hz | 30.5.282
SUF1INV1 | 21 | Temperature in the AC range | SU F1 INV1 | TmpCab_Acc | °C | 30.5.283
SUF1INV1 | 22 | Temperature in the DC range | SU F1 INV1 | TmpCab_Dcc | °C | 30.5.284
SUF1INV1 | 23 | Temperature in the electronics area | SU F1 INV1 | TmpCab_Rio | °C | 30.5.285
SUF1INV1 | 24 | Temperature in interior, maximum value | SU F1 INV1 | TmpCab_Max | °C | 30.5.286
SUF1INV1 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV1 | TmpStk_IgbtMax | °C | 30.5.287
SUF1INV1 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV1 | TmpStk_PcbMax | °C | 30.5.288
SUF1INV1 | 27 | Outside temperature | SU F1 INV1 | TmpExl | ?C | 30.5.289
SUF1INV1 | 28 | Temperature of the MV transformer | SU F1 INV1 | TmpTrf | °C | 30.5.290
SUF1INV1 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV1 | DcSw1Stt | "-" | 30.5.291
SUF1INV1 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV1 | DcSw2Stt | "-" | 30.5.292
SUF1INV1 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV1 | DcSw3Stt | "-" | 30.5.293
SUF1INV1 | 32 | Switching status of the AC circuit breaker | SU F1 INV1 | AcSwStt | "-" | 30.5.294
SUF1INV1 | 33 | Switching state of the capacitor contactor | SU F1 INV1 | CapacSwStt | "-" | 30.5.295
SUF1INV1 | 34 | Switching status of the pre-charging contactor | SU F1 INV1 | PrchrgSwStt | "-" | 30.5.296
SUF1INV1 | 35 | Feed-in hours | SU F1 INV1 | Cnt_TotFeedTm | "-" | 30.5.297
SUF1INV1 | 36 | Operating hours | SU F1 INV1 | Cnt_TotOpTm | "-" | 30.5.298
SUF1INV1 | 37 | DC energy drawn, total | SU F1 INV1 | Cnt_TotWatthIn | MWh | 30.5.299
SUF1INV1 | 38 | AC energy fed in, total | SU F1 INV1 | Cnt_TotWhOut | MWh | 30.5.300
SUF1INV1 | 39 | DC energy drawn that day | SU F1 INV1 | Cnt_WatthIn | MWh | 30.5.301
SUF1INV1 | 40 | AC energy fed in that day | SU F1 INV1 | Cnt_WhOut | MWh | 30.5.302
SUF1INV1 | 41 | Operating hours of the interior fan 1 | SU F1 INV1 | Cnt_FanCab1Tm | "-" | 30.5.303
SUF1INV1 | 42 | Operating hours of the interior fan 2 | SU F1 INV1 | Cnt_FanCab2Tm | "-" | 30.5.304
SUF1INV1 | 43 | Operating hours of the inverter bridge fan | SU F1 INV1 | Cnt_FanStkTm | "-" | 30.5.305
SUF1INV1 | 44 | Operating hours of the internal heating element | SU F1 INV1 | Cnt_HtCabTm | "-" | 30.5.306
SUF1INV1 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV1 | Cnt_HtLoExlTmpTm | "-" | 30.5.307
SUF1INV1 | 46 | Error location of the present error | SU F1 INV1 | ErrLcn | "-" | 30.5.308
SUF1INV1 | 47 | Error status of the inverter | SU F1 INV1 | ErrStt | "-" | 30.5.309
SUF1INV1 | 48 | Error number of the present error | SU F1 INV1 | ErrNo | "-" | 30.5.310
SUF1INV1 | 49 | Operating state of the inverter | SU F1 INV1 | OpStt | "-" | 30.5.311
SUF1INV1 | 50 | Switch status of the start-stop key switch | SU F1 INV1 | Rio_KeySw | "-" | 30.5.312
SUF1INV1 | 51 | Waiting time for grid connection | SU F1 INV1 | WaitGriTm | s | 30.5.313
SUF1INV1 | 52 | Inverter serial number | SU F1 INV1 | DevInf_SerNo | "-" | 30.5.314
SUF1INV1 | 53 | Switching status of the GFDI | SU F1 INV1 | GfdiSwStt | "-" | 30.5.315
SUF1INV1 | 54 | Active power, setpoint | SU F1 INV1 | WSpt | kW | 30.5.316
SUF1INV1 | 55 | Maximum apparent power, setpoint | SU F1 INV1 | VAMaxSpt | kVA | 30.5.317
SUF1INV1 | 56 | Reactive power, setpoint | SU F1 INV1 | VArSpt | kVAr | 30.5.318
SUF1INV1 | 57 | Power factor cos (phi), setpoint | SU F1 INV1 | PFSpt | "-" | 30.5.319
SUF1INV1 | 58 | Fast stop hermetic protection, pressure | SU F1 INV1 | TrfPro_Pres | "-" | 30.5.320
SUF1INV1 | 59 | Fast stop hermetic protection, temperature | SU F1 INV1 | TrfPro_TmpTrp | "-" | 30.5.321
SUF1INV1 | 60 | Hermetic protection, gas fill level | SU F1 INV1 | TrfPro_GasOilLev | "-" | 30.5.322
SUF1INV1 | 61 | Hermetic pressure, temperature warning | SU F1 INV1 | TrfPro_TmpWrn | "-" | 30.5.323
SUF1INV1 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV1 | TmpStk1_Igbt | °C | 30.5.324
SUF1INV1 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV1 | TmpStk2_Igbt | °C | 30.5.325
SUF1INV1 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV1 | TmpStk3_Igbt | °C | 30.5.326
SUF1INV1 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV1 | TmpStk1_Pcb | ?C | 30.5.327
SUF1INV1 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV1 | TmpStk2_Pcb | ?C | 30.5.328
SUF1INV1 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV1 | TmpStk3_Pcb | ?C | 30.5.329
SUF1INV1 | 68 | AC Energy Fed in the previous Day | SU F1 INV1 | Cnt_YstdWhOut | MWh | 30.5.330
SUF1INV1 | 69 | CPU running time since system start | SU F1 INV1 | Cpu1UpTime | s | 30.5.331
SUF1INV1 | 70 | Insulation resistance | SU F1 INV1 | PvGnd_RisIso | kOhm | 30.5.332
SUF1INV1 | 71 | MV transformer pressure | SU F1 INV1 | PresTrf | "-" | 30.5.333
SUF1INV1 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV1 | PresTrf_ErrStt | "-" | 30.5.334
SUF1INV1 | 73 | DC voltage DC plus to DC minus | SU F1 INV1 | DcMs_Vol_F | V | 30.5.335
SUF1INV1 | 74 | DC current inverter bridge 1 | SU F1 INV1 | DcMs_Amp_Stk1_F | A | 30.5.336
SUF1INV1 | 75 | DC current inverter bridge 2 | SU F1 INV1 | DcMs_Amp_Stk2_F | A | 30.5.337
SUF1INV1 | 76 | DC current inverter bridge 3 | SU F1 INV1 | DcMs_Amp_Stk3_F | A | 30.5.338
SUF1INV1 | 77 | DC current, total | SU F1 INV1 | DcMs_TotAmp_F | A | 30.5.339
SUF1INV1 | 78 | DC power, total | SU F1 INV1 | DcMs_TotWatt_F | kW | 30.5.340
SUF1INV1 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV1 | InvMs_DclVol_Stk1_F | V | 30.5.341
SUF1INV1 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV1 | InvMs_DclVol_Stk2_F | V | 30.5.342
SUF1INV1 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV1 | InvMs_DclVol_Stk3_F | V | 30.5.343
SUF1INV1 | 82 | AC current L1, total | SU F1 INV1 | InvMs_TotA_PhsA_F | A | 30.5.344
SUF1INV1 | 83 | AC current L2, total | SU F1 INV1 | InvMs_TotA_PhsB_F | A | 30.5.345
SUF1INV1 | 84 | AC current L3, total | SU F1 INV1 | InvMs_TotA_PhsC_F | A | 30.5.346
SUF1INV1 | 85 | Power factor (cos phi) | SU F1 INV1 | InvMs_PF_F | "-" | 30.5.347
SUF1INV1 | 86 | Active power, total | SU F1 INV1 | InvMs_TotW_F | kW | 30.5.348
SUF1INV1 | 87 | Reactive power, total | SU F1 INV1 | InvMs_TotVAr_F | kVAr | 30.5.349
SUF1INV1 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV1 | GriMs_V_PhsAB_F | V | 30.5.350
SUF1INV1 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV1 | GriMs_V_PhsBC_F | V | 30.5.351
SUF1INV1 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV1 | GriMs_V_PhsCA_F | V | 30.5.352
SUF1INV1 | 91 | Power frequency | SU F1 INV1 | GriMs_Hz_F | Hz | 30.5.353
SUF1INV1 | 92 | Temperature in the AC range | SU F1 INV1 | TmpCab_Acc_F | °C | 30.5.354
SUF1INV1 | 93 | Temperature in the DC range | SU F1 INV1 | TmpCab_Dcc_F | °C | 30.5.355
SUF1INV1 | 94 | Temperature in the electronics area | SU F1 INV1 | TmpCab_Rio_F | °C | 30.5.356
SUF1INV1 | 95 | Temperature in interior, maximum value | SU F1 INV1 | TmpCab_Max_F | °C | 30.5.357
SUF1INV1 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV1 | TmpStk_IgbtMax_F | °C | 30.5.358
SUF1INV1 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV1 | TmpStk_PcbMax_F | °C | 30.5.359
SUF1INV1 | 98 | Outside temperature | SU F1 INV1 | TmpExl_F | °C | 30.5.360
SUF1INV1 | 99 | Temperature of the MV transformer | SU F1 INV1 | TmpTrf_F | °C | 30.5.361
SUF1INV1 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV1 | TmpStk1_Igbt_F | °C | 30.5.362
SUF1INV1 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV1 | TmpStk2_Igbt_F | °C | 30.5.363
SUF1INV1 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV1 | TmpStk3_Igbt_F | °C | 30.5.364
SUF1INV1 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV1 | TmpStk1_Pcb_F | °C | 30.5.365
SUF1INV1 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV1 | TmpStk2_Pcb_F | °C | 30.5.366
SUF1INV1 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV1 | TmpStk3_Pcb_F | °C | 30.5.367
SUF1INV1 | 106 | MV transformer pressure | SU F1 INV1 | PresTrf_F | "-" | 30.5.368
SUF1INV1 | 110 | Switching status of the DC load-break switch | SU F1 INV1 | DcSwStt | "-" | 30.5.369
SUINV1JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV1 | Dat_UpdCnt_1 | "-" | 30.5.370
SUINV1JB1 | 2 | DC current input 1 | SU F1 INV1 | DcMs_Amp_01 | A | 30.5.371
SUINV1JB1 | 3 | DC current input 2 | SU F1 INV1 | DcMs_Amp_02 | A | 30.5.372
SUINV1JB1 | 4 | DC current input 3 | SU F1 INV1 | DcMs_Amp_03 | A | 30.5.373
SUINV1JB1 | 5 | DC current input 4 | SU F1 INV1 | DcMs_Amp_04 | A | 30.5.374
SUINV1JB1 | 6 | DC current input 5 | SU F1 INV1 | DcMs_Amp_05 | A | 30.5.375
SUINV1JB1 | 7 | DC current input 6 | SU F1 INV1 | DcMs_Amp_06 | A | 30.5.376
SUINV1JB1 | 8 | DC current input 7 | SU F1 INV1 | DcMs_Amp_07 | A | 30.5.377
SUINV1JB1 | 9 | DC current input 8 | SU F1 INV1 | DcMs_Amp_08 | A | 30.5.378
SUINV1JB1 | 10 | DC current input 9 | SU F1 INV1 | DcMs_Amp_09 | A | 30.5.379
SUINV1JB1 | 11 | DC current input 10 | SU F1 INV1 | DcMs_Amp_10 | A | 30.5.380
SUINV1JB1 | 12 | DC current input 11 | SU F1 INV1 | DcMs_Amp_11 | A | 30.5.381
SUINV1JB1 | 13 | DC current input 12 | SU F1 INV1 | DcMs_Amp_12 | A | 30.5.382
SUINV1JB1 | 14 | DC current input 13 | SU F1 INV1 | DcMs_Amp_13 | A | 30.5.383
SUINV1JB1 | 15 | DC current input 14 | SU F1 INV1 | DcMs_Amp_14 | A | 30.5.384
SUINV1JB1 | 16 | DC current input 15 | SU F1 INV1 | DcMs_Amp_15 | A | 30.5.385
SUINV1JB1 | 17 | DC current input 16 | SU F1 INV1 | DcMs_Amp_16 | A | 30.5.386
SUINV1JB1 | 18 | DC current input 1 | SU F1 INV1 | DcMs_Amp_01_F | A | 30.5.387
SUINV1JB1 | 19 | DC current input 2 | SU F1 INV1 | DcMs_Amp_02_F | A | 30.5.388
SUINV1JB1 | 20 | DC current input 3 | SU F1 INV1 | DcMs_Amp_03_F | A | 30.5.389
SUINV1JB1 | 21 | DC current input 4 | SU F1 INV1 | DcMs_Amp_04_F | A | 30.5.390
SUINV1JB1 | 22 | DC current input 5 | SU F1 INV1 | DcMs_Amp_05_F | A | 30.5.391
SUINV1JB1 | 23 | DC current input 6 | SU F1 INV1 | DcMs_Amp_06_F | A | 30.5.392
SUINV1JB1 | 24 | DC current input 7 | SU F1 INV1 | DcMs_Amp_07_F | A | 30.5.393
SUINV1JB1 | 25 | DC current input 8 | SU F1 INV1 | DcMs_Amp_08_F | A | 30.5.394
SUINV1JB1 | 26 | DC current input 9 | SU F1 INV1 | DcMs_Amp_09_F | A | 30.5.395
SUINV1JB1 | 27 | DC current input 10 | SU F1 INV1 | DcMs_Amp_10_F | A | 30.5.396
SUINV1JB1 | 28 | DC current input 11 | SU F1 INV1 | DcMs_Amp_11_F | A | 30.5.397
SUINV1JB1 | 29 | DC current input 12 | SU F1 INV1 | DcMs_Amp_12_F | A | 30.5.398
SUINV1JB1 | 30 | DC current input 13 | SU F1 INV1 | DcMs_Amp_13_F | A | 30.5.399
SUINV1JB1 | 31 | DC current input 14 | SU F1 INV1 | DcMs_Amp_14_F | A | 30.5.400
SUINV1JB1 | 32 | DC current input 15 | SU F1 INV1 | DcMs_Amp_15_F | A | 30.5.401
SUINV1JB1 | 33 | DC current input 16 | SU F1 INV1 | DcMs_Amp_16_F | A | 30.5.402
SUINV1JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV1 | Dat_UpdCnt_1 | "-" | 30.5.403
SUINV1JB2 | 2 | DC current input 1 | SU F1 INV1 | DcMs_Amp_01 | A | 30.5.404
SUINV1JB2 | 3 | DC current input 2 | SU F1 INV1 | DcMs_Amp_02 | A | 30.5.405
SUINV1JB2 | 4 | DC current input 3 | SU F1 INV1 | DcMs_Amp_03 | A | 30.5.406
SUINV1JB2 | 5 | DC current input 4 | SU F1 INV1 | DcMs_Amp_04 | A | 30.5.407
SUINV1JB2 | 6 | DC current input 5 | SU F1 INV1 | DcMs_Amp_05 | A | 30.5.408
SUINV1JB2 | 7 | DC current input 6 | SU F1 INV1 | DcMs_Amp_06 | A | 30.5.409
SUINV1JB2 | 8 | DC current input 7 | SU F1 INV1 | DcMs_Amp_07 | A | 30.5.410
SUINV1JB2 | 9 | DC current input 8 | SU F1 INV1 | DcMs_Amp_08 | A | 30.5.411
SUINV1JB2 | 10 | DC current input 9 | SU F1 INV1 | DcMs_Amp_09 | A | 30.5.412
SUINV1JB2 | 11 | DC current input 10 | SU F1 INV1 | DcMs_Amp_10 | A | 30.5.413
SUINV1JB2 | 12 | DC current input 11 | SU F1 INV1 | DcMs_Amp_11 | A | 30.5.414
SUINV1JB2 | 13 | DC current input 12 | SU F1 INV1 | DcMs_Amp_12 | A | 30.5.415
SUINV1JB2 | 14 | DC current input 13 | SU F1 INV1 | DcMs_Amp_13 | A | 30.5.416
SUINV1JB2 | 15 | DC current input 14 | SU F1 INV1 | DcMs_Amp_14 | A | 30.5.417
SUINV1JB2 | 16 | DC current input 15 | SU F1 INV1 | DcMs_Amp_15 | A | 30.5.418
SUINV1JB2 | 17 | DC current input 16 | SU F1 INV1 | DcMs_Amp_16 | A | 30.5.419
SUINV1JB2 | 18 | DC current input 1 | SU F1 INV1 | DcMs_Amp_01_F | A | 30.5.420
SUINV1JB2 | 19 | DC current input 2 | SU F1 INV1 | DcMs_Amp_02_F | A | 30.5.421
SUINV1JB2 | 20 | DC current input 3 | SU F1 INV1 | DcMs_Amp_03_F | A | 30.5.422
SUINV1JB2 | 21 | DC current input 4 | SU F1 INV1 | DcMs_Amp_04_F | A | 30.5.423
SUINV1JB2 | 22 | DC current input 5 | SU F1 INV1 | DcMs_Amp_05_F | A | 30.5.424
SUINV1JB2 | 23 | DC current input 6 | SU F1 INV1 | DcMs_Amp_06_F | A | 30.5.425
SUINV1JB2 | 24 | DC current input 7 | SU F1 INV1 | DcMs_Amp_07_F | A | 30.5.426
SUINV1JB2 | 25 | DC current input 8 | SU F1 INV1 | DcMs_Amp_08_F | A | 30.5.427
SUINV1JB2 | 26 | DC current input 9 | SU F1 INV1 | DcMs_Amp_09_F | A | 30.5.428
SUINV1JB2 | 27 | DC current input 10 | SU F1 INV1 | DcMs_Amp_10_F | A | 30.5.429
SUINV1JB2 | 28 | DC current input 11 | SU F1 INV1 | DcMs_Amp_11_F | A | 30.5.430
SUINV1JB2 | 29 | DC current input 12 | SU F1 INV1 | DcMs_Amp_12_F | A | 30.5.431
SUINV1JB2 | 30 | DC current input 13 | SU F1 INV1 | DcMs_Amp_13_F | A | 30.5.432
SUINV1JB2 | 31 | DC current input 14 | SU F1 INV1 | DcMs_Amp_14_F | A | 30.5.433
SUINV1JB2 | 32 | DC current input 15 | SU F1 INV1 | DcMs_Amp_15_F | A | 30.5.434
SUINV1JB2 | 33 | DC current input 16 | SU F1 INV1 | DcMs_Amp_16_F | A | 30.5.435
SUF1INV2 | 1 | DC voltage DC plus to DC minus | SU F1 INV2 | DcMs_Vol | V | 30.5.436
SUF1INV2 | 2 | DC current inverter bridge 1 | SU F1 INV2 | DcMs_Amp_Stk1 | A | 30.5.437
SUF1INV2 | 3 | DC current inverter bridge 2 | SU F1 INV2 | DcMs_Amp_Stk2 | A | 30.5.438
SUF1INV2 | 4 | DC current inverter bridge 3 | SU F1 INV2 | DcMs_Amp_Stk3 | A | 30.5.439
SUF1INV2 | 5 | DC current, total | SU F1 INV2 | DcMs_TotAmp | A | 30.5.440
SUF1INV2 | 6 | DC power, total | SU F1 INV2 | DcMs_TotWatt | kW | 30.5.441
SUF1INV2 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV2 | InvMs_DclVol_Stk1 | V | 30.5.442
SUF1INV2 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV2 | InvMs_DclVol_Stk2 | V | 30.5.443
SUF1INV2 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV2 | InvMs_DclVol_Stk3 | V | 30.5.444
SUF1INV2 | 10 | AC current L1, total | SU F1 INV2 | InvMs_TotA_PhsA | A | 30.5.445
SUF1INV2 | 11 | AC current L2, total | SU F1 INV2 | InvMs_TotA_PhsB | A | 30.5.446
SUF1INV2 | 12 | AC current L3, total | SU F1 INV2 | InvMs_TotA_PhsC | A | 30.5.447
SUF1INV2 | 13 | Power factor (cos phi) | SU F1 INV2 | InvMs_PF | "-" | 30.5.448
SUF1INV2 | 14 | Apparent power, total | SU F1 INV2 | InvMs_TotVA | kVA | 30.5.449
SUF1INV2 | 15 | Active power, total | SU F1 INV2 | InvMs_TotW | kW | 30.5.450
SUF1INV2 | 16 | Reactive power, total | SU F1 INV2 | InvMs_TotVAr | kVAr | 30.5.451
SUF1INV2 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV2 | GriMs_V_PhsAB | V | 30.5.452
SUF1INV2 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV2 | GriMs_V_PhsBC | V | 30.5.453
SUF1INV2 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV2 | GriMs_V_PhsCA | V | 30.5.454
SUF1INV2 | 20 | Power frequency | SU F1 INV2 | GriMs_Hz | Hz | 30.5.455
SUF1INV2 | 21 | Temperature in the AC range | SU F1 INV2 | TmpCab_Acc | °C | 30.5.456
SUF1INV2 | 22 | Temperature in the DC range | SU F1 INV2 | TmpCab_Dcc | °C | 30.5.457
SUF1INV2 | 23 | Temperature in the electronics area | SU F1 INV2 | TmpCab_Rio | °C | 30.5.458
SUF1INV2 | 24 | Temperature in interior, maximum value | SU F1 INV2 | TmpCab_Max | °C | 30.5.459
SUF1INV2 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV2 | TmpStk_IgbtMax | °C | 30.5.460
SUF1INV2 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV2 | TmpStk_PcbMax | °C | 30.5.461
SUF1INV2 | 27 | Outside temperature | SU F1 INV2 | TmpExl | °C | 30.5.462
SUF1INV2 | 28 | Temperature of the MV transformer | SU F1 INV2 | TmpTrf | °C | 30.5.463
SUF1INV2 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV2 | DcSw1Stt | "-" | 30.5.464
SUF1INV2 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV2 | DcSw2Stt | "-" | 30.5.465
SUF1INV2 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV2 | DcSw3Stt | "-" | 30.5.466
SUF1INV2 | 32 | Switching status of the AC circuit breaker | SU F1 INV2 | AcSwStt | "-" | 30.5.467
SUF1INV2 | 33 | Switching state of the capacitor contactor | SU F1 INV2 | CapacSwStt | "-" | 30.5.468
SUF1INV2 | 34 | Switching status of the pre-charging contactor | SU F1 INV2 | PrchrgSwStt | "-" | 30.5.469
SUF1INV2 | 35 | Feed-in hours | SU F1 INV2 | Cnt_TotFeedTm | "-" | 30.5.470
SUF1INV2 | 36 | Operating hours | SU F1 INV2 | Cnt_TotOpTm | "-" | 30.5.471
SUF1INV2 | 37 | DC energy drawn, total | SU F1 INV2 | Cnt_TotWatthIn | MWh | 30.5.472
SUF1INV2 | 38 | AC energy fed in, total | SU F1 INV2 | Cnt_TotWhOut | MWh | 30.5.473
SUF1INV2 | 39 | DC energy drawn that day | SU F1 INV2 | Cnt_WatthIn | MWh | 30.5.474
SUF1INV2 | 40 | AC energy fed in that day | SU F1 INV2 | Cnt_WhOut | MWh | 30.5.475
SUF1INV2 | 41 | Operating hours of the interior fan 1 | SU F1 INV2 | Cnt_FanCab1Tm | "-" | 30.5.476
SUF1INV2 | 42 | Operating hours of the interior fan 2 | SU F1 INV2 | Cnt_FanCab2Tm | "-" | 30.5.477
SUF1INV2 | 43 | Operating hours of the inverter bridge fan | SU F1 INV2 | Cnt_FanStkTm | "-" | 30.5.478
SUF1INV2 | 44 | Operating hours of the internal heating element | SU F1 INV2 | Cnt_HtCabTm | "-" | 30.5.479
SUF1INV2 | 45 | Operating hours of the -40°C internal heating element | SU F1 INV2 | Cnt_HtLoExlTmpTm | "-" | 30.5.480
SUF1INV2 | 46 | Error location of the present error | SU F1 INV2 | ErrLcn | "-" | 30.5.481
SUF1INV2 | 47 | Error status of the inverter | SU F1 INV2 | ErrStt | "-" | 30.5.482
SUF1INV2 | 48 | Error number of the present error | SU F1 INV2 | ErrNo | "-" | 30.5.483
SUF1INV2 | 49 | Operating state of the inverter | SU F1 INV2 | OpStt | "-" | 30.5.484
SUF1INV2 | 50 | Switch status of the start-stop key switch | SU F1 INV2 | Rio_KeySw | "-" | 30.5.485
SUF1INV2 | 51 | Waiting time for grid connection | SU F1 INV2 | WaitGriTm | s | 30.5.486
SUF1INV2 | 52 | Inverter serial number | SU F1 INV2 | DevInf_SerNo | "-" | 30.5.487
SUF1INV2 | 53 | Switching status of the GFDI | SU F1 INV2 | GfdiSwStt | "-" | 30.5.488
SUF1INV2 | 54 | Active power, setpoint | SU F1 INV2 | WSpt | kW | 30.5.489
SUF1INV2 | 55 | Maximum apparent power, setpoint | SU F1 INV2 | VAMaxSpt | kVA | 30.5.490
SUF1INV2 | 56 | Reactive power, setpoint | SU F1 INV2 | VArSpt | kVAr | 30.5.491
SUF1INV2 | 57 | Power factor cos (phi), setpoint | SU F1 INV2 | PFSpt | "-" | 30.5.492
SUF1INV2 | 58 | Fast stop hermetic protection, pressure | SU F1 INV2 | TrfPro_Pres | "-" | 30.5.493
SUF1INV2 | 59 | Fast stop hermetic protection, temperature | SU F1 INV2 | TrfPro_TmpTrp | "-" | 30.5.494
SUF1INV2 | 60 | Hermetic protection, gas fill level | SU F1 INV2 | TrfPro_GasOilLev | "-" | 30.5.495
SUF1INV2 | 61 | Hermetic pressure, temperature warning | SU F1 INV2 | TrfPro_TmpWrn | "-" | 30.5.496
SUF1INV2 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV2 | TmpStk1_Igbt | °C | 30.5.497
SUF1INV2 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV2 | TmpStk2_Igbt | °C | 30.5.498
SUF1INV2 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV2 | TmpStk3_Igbt | °C | 30.5.499
SUF1INV2 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV2 | TmpStk1_Pcb | °C | 30.5.500
SUF1INV2 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV2 | TmpStk2_Pcb | °C | 30.5.501
SUF1INV2 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV2 | TmpStk3_Pcb | °C | 30.5.502
SUF1INV2 | 68 | AC Energy Fed in the previous Day | SU F1 INV2 | Cnt_YstdWhOut | MWh | 30.5.503
SUF1INV2 | 69 | CPU running time since system start | SU F1 INV2 | Cpu1UpTime | s | 30.5.504
SUF1INV2 | 70 | Insulation resistance | SU F1 INV2 | PvGnd_RisIso | kOhm | 30.5.505
SUF1INV2 | 71 | MV transformer pressure | SU F1 INV2 | PresTrf | "-" | 30.5.506
SUF1INV2 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV2 | PresTrf_ErrStt | "-" | 30.5.507
SUF1INV2 | 73 | DC voltage DC plus to DC minus | SU F1 INV2 | DcMs_Vol_F | V | 30.5.508
SUF1INV2 | 74 | DC current inverter bridge 1 | SU F1 INV2 | DcMs_Amp_Stk1_F | A | 30.5.509
SUF1INV2 | 75 | DC current inverter bridge 2 | SU F1 INV2 | DcMs_Amp_Stk2_F | A | 30.5.510
SUF1INV2 | 76 | DC current inverter bridge 3 | SU F1 INV2 | DcMs_Amp_Stk3_F | A | 30.5.511
SUF1INV2 | 77 | DC current, total | SU F1 INV2 | DcMs_TotAmp_F | A | 30.5.512
SUF1INV2 | 78 | DC power, total | SU F1 INV2 | DcMs_TotWatt_F | kW | 30.5.513
SUF1INV2 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV2 | InvMs_DclVol_Stk1_F | V | 30.5.514
SUF1INV2 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV2 | InvMs_DclVol_Stk2_F | V | 30.5.515
SUF1INV2 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV2 | InvMs_DclVol_Stk3_F | V | 30.5.516
SUF1INV2 | 82 | AC current L1, total | SU F1 INV2 | InvMs_TotA_PhsA_F | A | 30.5.517
SUF1INV2 | 83 | AC current L2, total | SU F1 INV2 | InvMs_TotA_PhsB_F | A | 30.5.518
SUF1INV2 | 84 | AC current L3, total | SU F1 INV2 | InvMs_TotA_PhsC_F | A | 30.5.519
SUF1INV2 | 85 | Power factor (cos phi) | SU F1 INV2 | InvMs_PF_F | "-" | 30.5.520
SUF1INV2 | 86 | Active power, total | SU F1 INV2 | InvMs_TotW_F | kW | 30.5.521
SUF1INV2 | 87 | Reactive power, total | SU F1 INV2 | InvMs_TotVAr_F | kVAr | 30.5.522
SUF1INV2 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV2 | GriMs_V_PhsAB_F | V | 30.5.523
SUF1INV2 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV2 | GriMs_V_PhsBC_F | V | 30.5.524
SUF1INV2 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV2 | GriMs_V_PhsCA_F | V | 30.5.525
SUF1INV2 | 91 | Power frequency | SU F1 INV2 | GriMs_Hz_F | Hz | 30.5.526
SUF1INV2 | 92 | Temperature in the AC range | SU F1 INV2 | TmpCab_Acc_F | °C | 30.5.527
SUF1INV2 | 93 | Temperature in the DC range | SU F1 INV2 | TmpCab_Dcc_F | °C | 30.5.528
SUF1INV2 | 94 | Temperature in the electronics area | SU F1 INV2 | TmpCab_Rio_F | °C | 30.5.529
SUF1INV2 | 95 | Temperature in interior, maximum value | SU F1 INV2 | TmpCab_Max_F | °C | 30.5.530
SUF1INV2 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV2 | TmpStk_IgbtMax_F | °C | 30.5.531
SUF1INV2 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV2 | TmpStk_PcbMax_F | °C | 30.5.532
SUF1INV2 | 98 | Outside temperature | SU F1 INV2 | TmpExl_F | °C | 30.5.533
SUF1INV2 | 99 | Temperature of the MV transformer | SU F1 INV2 | TmpTrf_F | °C | 30.5.534
SUF1INV2 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV2 | TmpStk1_Igbt_F | °C | 30.5.535
SUF1INV2 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV2 | TmpStk2_Igbt_F | °C | 30.5.536
SUF1INV2 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV2 | TmpStk3_Igbt_F | °C | 30.5.537
SUF1INV2 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV2 | TmpStk1_Pcb_F | °C | 30.5.538
SUF1INV2 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV2 | TmpStk2_Pcb_F | °C | 30.5.539
SUF1INV2 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV2 | TmpStk3_Pcb_F | °C | 30.5.540
SUF1INV2 | 106 | MV transformer pressure | SU F1 INV2 | PresTrf_F | "-" | 30.5.541
SUF1INV2 | 110 | Switching status of the DC load-break switch | SU F1 INV2 | DcSwStt | "-" | 30.5.542
SUINV2JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV2 | Dat_UpdCnt_1 | "-" | 30.5.543
SUINV2JB1 | 2 | DC current input 1 | SU F1 INV2 | DcMs_Amp_01 | A | 30.5.544
SUINV2JB1 | 3 | DC current input 2 | SU F1 INV2 | DcMs_Amp_02 | A | 30.5.545
SUINV2JB1 | 4 | DC current input 3 | SU F1 INV2 | DcMs_Amp_03 | A | 30.5.546
SUINV2JB1 | 5 | DC current input 4 | SU F1 INV2 | DcMs_Amp_04 | A | 30.5.547
SUINV2JB1 | 6 | DC current input 5 | SU F1 INV2 | DcMs_Amp_05 | A | 30.5.548
SUINV2JB1 | 7 | DC current input 6 | SU F1 INV2 | DcMs_Amp_06 | A | 30.5.549
SUINV2JB1 | 8 | DC current input 7 | SU F1 INV2 | DcMs_Amp_07 | A | 30.5.550
SUINV2JB1 | 9 | DC current input 8 | SU F1 INV2 | DcMs_Amp_08 | A | 30.5.551
SUINV2JB1 | 10 | DC current input 9 | SU F1 INV2 | DcMs_Amp_09 | A | 30.5.552
SUINV2JB1 | 11 | DC current input 10 | SU F1 INV2 | DcMs_Amp_10 | A | 30.5.553
SUINV2JB1 | 12 | DC current input 11 | SU F1 INV2 | DcMs_Amp_11 | A | 30.5.554
SUINV2JB1 | 13 | DC current input 12 | SU F1 INV2 | DcMs_Amp_12 | A | 30.5.555
SUINV2JB1 | 14 | DC current input 13 | SU F1 INV2 | DcMs_Amp_13 | A | 30.5.556
SUINV2JB1 | 15 | DC current input 14 | SU F1 INV2 | DcMs_Amp_14 | A | 30.5.557
SUINV2JB1 | 16 | DC current input 15 | SU F1 INV2 | DcMs_Amp_15 | A | 30.5.558
SUINV2JB1 | 17 | DC current input 16 | SU F1 INV2 | DcMs_Amp_16 | A | 30.5.559
SUINV2JB1 | 18 | DC current input 1 | SU F1 INV2 | DcMs_Amp_01_F | A | 30.5.560
SUINV2JB1 | 19 | DC current input 2 | SU F1 INV2 | DcMs_Amp_02_F | A | 30.5.561
SUINV2JB1 | 20 | DC current input 3 | SU F1 INV2 | DcMs_Amp_03_F | A | 30.5.562
SUINV2JB1 | 21 | DC current input 4 | SU F1 INV2 | DcMs_Amp_04_F | A | 30.5.563
SUINV2JB1 | 22 | DC current input 5 | SU F1 INV2 | DcMs_Amp_05_F | A | 30.5.564
SUINV2JB1 | 23 | DC current input 6 | SU F1 INV2 | DcMs_Amp_06_F | A | 30.5.565
SUINV2JB1 | 24 | DC current input 7 | SU F1 INV2 | DcMs_Amp_07_F | A | 30.5.566
SUINV2JB1 | 25 | DC current input 8 | SU F1 INV2 | DcMs_Amp_08_F | A | 30.5.567
SUINV2JB1 | 26 | DC current input 9 | SU F1 INV2 | DcMs_Amp_09_F | A | 30.5.568
SUINV2JB1 | 27 | DC current input 10 | SU F1 INV2 | DcMs_Amp_10_F | A | 30.5.569
SUINV2JB1 | 28 | DC current input 11 | SU F1 INV2 | DcMs_Amp_11_F | A | 30.5.570
SUINV2JB1 | 29 | DC current input 12 | SU F1 INV2 | DcMs_Amp_12_F | A | 30.5.571
SUINV2JB1 | 30 | DC current input 13 | SU F1 INV2 | DcMs_Amp_13_F | A | 30.5.572
SUINV2JB1 | 31 | DC current input 14 | SU F1 INV2 | DcMs_Amp_14_F | A | 30.5.573
SUINV2JB1 | 32 | DC current input 15 | SU F1 INV2 | DcMs_Amp_15_F | A | 30.5.574
SUINV2JB1 | 33 | DC current input 16 | SU F1 INV2 | DcMs_Amp_16_F | A | 30.5.575
SUINV2JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV2 | Dat_UpdCnt_1 | "-" | 30.5.576
SUINV2JB2 | 2 | DC current input 1 | SU F1 INV2 | DcMs_Amp_01 | A | 30.5.577
SUINV2JB2 | 3 | DC current input 2 | SU F1 INV2 | DcMs_Amp_02 | A | 30.5.578
SUINV2JB2 | 4 | DC current input 3 | SU F1 INV2 | DcMs_Amp_03 | A | 30.5.579
SUINV2JB2 | 5 | DC current input 4 | SU F1 INV2 | DcMs_Amp_04 | A | 30.5.580
SUINV2JB2 | 6 | DC current input 5 | SU F1 INV2 | DcMs_Amp_05 | A | 30.5.581
SUINV2JB2 | 7 | DC current input 6 | SU F1 INV2 | DcMs_Amp_06 | A | 30.5.582
SUINV2JB2 | 8 | DC current input 7 | SU F1 INV2 | DcMs_Amp_07 | A | 30.5.583
SUINV2JB2 | 9 | DC current input 8 | SU F1 INV2 | DcMs_Amp_08 | A | 30.5.584
SUINV2JB2 | 10 | DC current input 9 | SU F1 INV2 | DcMs_Amp_09 | A | 30.5.585
SUINV2JB2 | 11 | DC current input 10 | SU F1 INV2 | DcMs_Amp_10 | A | 30.5.586
SUINV2JB2 | 12 | DC current input 11 | SU F1 INV2 | DcMs_Amp_11 | A | 30.5.587
SUINV2JB2 | 13 | DC current input 12 | SU F1 INV2 | DcMs_Amp_12 | A | 30.5.588
SUINV2JB2 | 14 | DC current input 13 | SU F1 INV2 | DcMs_Amp_13 | A | 30.5.589
SUINV2JB2 | 15 | DC current input 14 | SU F1 INV2 | DcMs_Amp_14 | A | 30.5.590
SUINV2JB2 | 16 | DC current input 15 | SU F1 INV2 | DcMs_Amp_15 | A | 30.5.591
SUINV2JB2 | 17 | DC current input 16 | SU F1 INV2 | DcMs_Amp_16 | A | 30.5.592
SUINV2JB2 | 18 | DC current input 1 | SU F1 INV2 | DcMs_Amp_01_F | A | 30.5.593
SUINV2JB2 | 19 | DC current input 2 | SU F1 INV2 | DcMs_Amp_02_F | A | 30.5.594
SUINV2JB2 | 20 | DC current input 3 | SU F1 INV2 | DcMs_Amp_03_F | A | 30.5.595
SUINV2JB2 | 21 | DC current input 4 | SU F1 INV2 | DcMs_Amp_04_F | A | 30.5.596
SUINV2JB2 | 22 | DC current input 5 | SU F1 INV2 | DcMs_Amp_05_F | A | 30.5.597
SUINV2JB2 | 23 | DC current input 6 | SU F1 INV2 | DcMs_Amp_06_F | A | 30.5.598
SUINV2JB2 | 24 | DC current input 7 | SU F1 INV2 | DcMs_Amp_07_F | A | 30.5.599
SUINV2JB2 | 25 | DC current input 8 | SU F1 INV2 | DcMs_Amp_08_F | A | 30.5.600
SUINV2JB2 | 26 | DC current input 9 | SU F1 INV2 | DcMs_Amp_09_F | A | 30.5.601
SUINV2JB2 | 27 | DC current input 10 | SU F1 INV2 | DcMs_Amp_10_F | A | 30.5.602
SUINV2JB2 | 28 | DC current input 11 | SU F1 INV2 | DcMs_Amp_11_F | A | 30.5.603
SUINV2JB2 | 29 | DC current input 12 | SU F1 INV2 | DcMs_Amp_12_F | A | 30.5.604
SUINV2JB2 | 30 | DC current input 13 | SU F1 INV2 | DcMs_Amp_13_F | A | 30.5.605
SUINV2JB2 | 31 | DC current input 14 | SU F1 INV2 | DcMs_Amp_14_F | A | 30.5.606
SUINV2JB2 | 32 | DC current input 15 | SU F1 INV2 | DcMs_Amp_15_F | A | 30.5.607
SUINV2JB2 | 33 | DC current input 16 | SU F1 INV2 | DcMs_Amp_16_F | A | 30.5.608
SUF1INV3 | 1 | DC voltage DC plus to DC minus | SU F1 INV3 | DcMs_Vol | V | 30.5.609
SUF1INV3 | 2 | DC current inverter bridge 1 | SU F1 INV3 | DcMs_Amp_Stk1 | A | 30.5.610
SUF1INV3 | 3 | DC current inverter bridge 2 | SU F1 INV3 | DcMs_Amp_Stk2 | A | 30.5.611
SUF1INV3 | 4 | DC current inverter bridge 3 | SU F1 INV3 | DcMs_Amp_Stk3 | A | 30.5.612
SUF1INV3 | 5 | DC current, total | SU F1 INV3 | DcMs_TotAmp | A | 30.5.613
SUF1INV3 | 6 | DC power, total | SU F1 INV3 | DcMs_TotWatt | kW | 30.5.614
SUF1INV3 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV3 | InvMs_DclVol_Stk1 | V | 30.5.615
SUF1INV3 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV3 | InvMs_DclVol_Stk2 | V | 30.5.616
SUF1INV3 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV3 | InvMs_DclVol_Stk3 | V | 30.5.617
SUF1INV3 | 10 | AC current L1, total | SU F1 INV3 | InvMs_TotA_PhsA | A | 30.5.618
SUF1INV3 | 11 | AC current L2, total | SU F1 INV3 | InvMs_TotA_PhsB | A | 30.5.619
SUF1INV3 | 12 | AC current L3, total | SU F1 INV3 | InvMs_TotA_PhsC | A | 30.5.620
SUF1INV3 | 13 | Power factor (cos phi) | SU F1 INV3 | InvMs_PF | "-" | 30.5.621
SUF1INV3 | 14 | Apparent power, total | SU F1 INV3 | InvMs_TotVA | kVA | 30.5.622
SUF1INV3 | 15 | Active power, total | SU F1 INV3 | InvMs_TotW | kW | 30.5.623
SUF1INV3 | 16 | Reactive power, total | SU F1 INV3 | InvMs_TotVAr | kVAr | 30.5.624
SUF1INV3 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV3 | GriMs_V_PhsAB | V | 30.5.625
SUF1INV3 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV3 | GriMs_V_PhsBC | V | 30.5.626
SUF1INV3 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV3 | GriMs_V_PhsCA | V | 30.5.627
SUF1INV3 | 20 | Power frequency | SU F1 INV3 | GriMs_Hz | Hz | 30.5.628
SUF1INV3 | 21 | Temperature in the AC range | SU F1 INV3 | TmpCab_Acc | °C | 30.5.629
SUF1INV3 | 22 | Temperature in the DC range | SU F1 INV3 | TmpCab_Dcc | °C | 30.5.630
SUF1INV3 | 23 | Temperature in the electronics area | SU F1 INV3 | TmpCab_Rio | °C | 30.5.631
SUF1INV3 | 24 | Temperature in interior, maximum value | SU F1 INV3 | TmpCab_Max | °C | 30.5.632
SUF1INV3 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV3 | TmpStk_IgbtMax | °C | 30.5.633
SUF1INV3 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV3 | TmpStk_PcbMax | °C | 30.5.634
SUF1INV3 | 27 | Outside temperature | SU F1 INV3 | TmpExl | ?C | 30.5.635
SUF1INV3 | 28 | Temperature of the MV transformer | SU F1 INV3 | TmpTrf | °C | 30.5.636
SUF1INV3 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV3 | DcSw1Stt | "-" | 30.5.637
SUF1INV3 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV3 | DcSw2Stt | "-" | 30.5.638
SUF1INV3 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV3 | DcSw3Stt | "-" | 30.5.639
SUF1INV3 | 32 | Switching status of the AC circuit breaker | SU F1 INV3 | AcSwStt | "-" | 30.5.640
SUF1INV3 | 33 | Switching state of the capacitor contactor | SU F1 INV3 | CapacSwStt | "-" | 30.5.641
SUF1INV3 | 34 | Switching status of the pre-charging contactor | SU F1 INV3 | PrchrgSwStt | "-" | 30.5.642
SUF1INV3 | 35 | Feed-in hours | SU F1 INV3 | Cnt_TotFeedTm | "-" | 30.5.643
SUF1INV3 | 36 | Operating hours | SU F1 INV3 | Cnt_TotOpTm | "-" | 30.5.644
SUF1INV3 | 37 | DC energy drawn, total | SU F1 INV3 | Cnt_TotWatthIn | MWh | 30.5.645
SUF1INV3 | 38 | AC energy fed in, total | SU F1 INV3 | Cnt_TotWhOut | MWh | 30.5.646
SUF1INV3 | 39 | DC energy drawn that day | SU F1 INV3 | Cnt_WatthIn | MWh | 30.5.647
SUF1INV3 | 40 | AC energy fed in that day | SU F1 INV3 | Cnt_WhOut | MWh | 30.5.648
SUF1INV3 | 41 | Operating hours of the interior fan 1 | SU F1 INV3 | Cnt_FanCab1Tm | "-" | 30.5.649
SUF1INV3 | 42 | Operating hours of the interior fan 2 | SU F1 INV3 | Cnt_FanCab2Tm | "-" | 30.5.650
SUF1INV3 | 43 | Operating hours of the inverter bridge fan | SU F1 INV3 | Cnt_FanStkTm | "-" | 30.5.651
SUF1INV3 | 44 | Operating hours of the internal heating element | SU F1 INV3 | Cnt_HtCabTm | "-" | 30.5.652
SUF1INV3 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV3 | Cnt_HtLoExlTmpTm | "-" | 30.5.653
SUF1INV3 | 46 | Error location of the present error | SU F1 INV3 | ErrLcn | "-" | 30.5.654
SUF1INV3 | 47 | Error status of the inverter | SU F1 INV3 | ErrStt | "-" | 30.5.655
SUF1INV3 | 48 | Error number of the present error | SU F1 INV3 | ErrNo | "-" | 30.5.656
SUF1INV3 | 49 | Operating state of the inverter | SU F1 INV3 | OpStt | "-" | 30.5.657
SUF1INV3 | 50 | Switch status of the start-stop key switch | SU F1 INV3 | Rio_KeySw | "-" | 30.5.658
SUF1INV3 | 51 | Waiting time for grid connection | SU F1 INV3 | WaitGriTm | s | 30.5.659
SUF1INV3 | 52 | Inverter serial number | SU F1 INV3 | DevInf_SerNo | "-" | 30.5.660
SUF1INV3 | 53 | Switching status of the GFDI | SU F1 INV3 | GfdiSwStt | "-" | 30.5.661
SUF1INV3 | 54 | Active power, setpoint | SU F1 INV3 | WSpt | kW | 30.5.662
SUF1INV3 | 55 | Maximum apparent power, setpoint | SU F1 INV3 | VAMaxSpt | kVA | 30.5.663
SUF1INV3 | 56 | Reactive power, setpoint | SU F1 INV3 | VArSpt | kVAr | 30.5.664
SUF1INV3 | 57 | Power factor cos (phi), setpoint | SU F1 INV3 | PFSpt | "-" | 30.5.665
SUF1INV3 | 58 | Fast stop hermetic protection, pressure | SU F1 INV3 | TrfPro_Pres | "-" | 30.5.666
SUF1INV3 | 59 | Fast stop hermetic protection, temperature | SU F1 INV3 | TrfPro_TmpTrp | "-" | 30.5.667
SUF1INV3 | 60 | Hermetic protection, gas fill level | SU F1 INV3 | TrfPro_GasOilLev | "-" | 30.5.668
SUF1INV3 | 61 | Hermetic pressure, temperature warning | SU F1 INV3 | TrfPro_TmpWrn | "-" | 30.5.669
SUF1INV3 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV3 | TmpStk1_Igbt | °C | 30.5.670
SUF1INV3 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV3 | TmpStk2_Igbt | °C | 30.5.671
SUF1INV3 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV3 | TmpStk3_Igbt | °C | 30.5.672
SUF1INV3 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV3 | TmpStk1_Pcb | ?C | 30.5.673
SUF1INV3 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV3 | TmpStk2_Pcb | ?C | 30.5.674
SUF1INV3 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV3 | TmpStk3_Pcb | ?C | 30.5.675
SUF1INV3 | 68 | AC Energy Fed in the previous Day | SU F1 INV3 | Cnt_YstdWhOut | MWh | 30.5.676
SUF1INV3 | 69 | CPU running time since system start | SU F1 INV3 | Cpu1UpTime | s | 30.5.677
SUF1INV3 | 70 | Insulation resistance | SU F1 INV3 | PvGnd_RisIso | kOhm | 30.5.678
SUF1INV3 | 71 | MV transformer pressure | SU F1 INV3 | PresTrf | "-" | 30.5.679
SUF1INV3 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV3 | PresTrf_ErrStt | "-" | 30.5.680
SUF1INV3 | 73 | DC voltage DC plus to DC minus | SU F1 INV3 | DcMs_Vol_F | V | 30.5.681
SUF1INV3 | 74 | DC current inverter bridge 1 | SU F1 INV3 | DcMs_Amp_Stk1_F | A | 30.5.682
SUF1INV3 | 75 | DC current inverter bridge 2 | SU F1 INV3 | DcMs_Amp_Stk2_F | A | 30.5.683
SUF1INV3 | 76 | DC current inverter bridge 3 | SU F1 INV3 | DcMs_Amp_Stk3_F | A | 30.5.684
SUF1INV3 | 77 | DC current, total | SU F1 INV3 | DcMs_TotAmp_F | A | 30.5.685
SUF1INV3 | 78 | DC power, total | SU F1 INV3 | DcMs_TotWatt_F | kW | 30.5.686
SUF1INV3 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV3 | InvMs_DclVol_Stk1_F | V | 30.5.687
SUF1INV3 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV3 | InvMs_DclVol_Stk2_F | V | 30.5.688
SUF1INV3 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV3 | InvMs_DclVol_Stk3_F | V | 30.5.689
SUF1INV3 | 82 | AC current L1, total | SU F1 INV3 | InvMs_TotA_PhsA_F | A | 30.5.690
SUF1INV3 | 83 | AC current L2, total | SU F1 INV3 | InvMs_TotA_PhsB_F | A | 30.5.691
SUF1INV3 | 84 | AC current L3, total | SU F1 INV3 | InvMs_TotA_PhsC_F | A | 30.5.692
SUF1INV3 | 85 | Power factor (cos phi) | SU F1 INV3 | InvMs_PF_F | "-" | 30.5.693
SUF1INV3 | 86 | Active power, total | SU F1 INV3 | InvMs_TotW_F | kW | 30.5.694
SUF1INV3 | 87 | Reactive power, total | SU F1 INV3 | InvMs_TotVAr_F | kVAr | 30.5.695
SUF1INV3 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV3 | GriMs_V_PhsAB_F | V | 30.5.696
SUF1INV3 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV3 | GriMs_V_PhsBC_F | V | 30.5.697
SUF1INV3 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV3 | GriMs_V_PhsCA_F | V | 30.5.698
SUF1INV3 | 91 | Power frequency | SU F1 INV3 | GriMs_Hz_F | Hz | 30.5.699
SUF1INV3 | 92 | Temperature in the AC range | SU F1 INV3 | TmpCab_Acc_F | °C | 30.5.700
SUF1INV3 | 93 | Temperature in the DC range | SU F1 INV3 | TmpCab_Dcc_F | °C | 30.5.701
SUF1INV3 | 94 | Temperature in the electronics area | SU F1 INV3 | TmpCab_Rio_F | °C | 30.5.702
SUF1INV3 | 95 | Temperature in interior, maximum value | SU F1 INV3 | TmpCab_Max_F | °C | 30.5.703
SUF1INV3 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV3 | TmpStk_IgbtMax_F | °C | 30.5.704
SUF1INV3 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV3 | TmpStk_PcbMax_F | °C | 30.5.705
SUF1INV3 | 98 | Outside temperature | SU F1 INV3 | TmpExl_F | ?C | 30.5.706
SUF1INV3 | 99 | Temperature of the MV transformer | SU F1 INV3 | TmpTrf_F | °C | 30.5.707
SUF1INV3 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV3 | TmpStk1_Igbt_F | °C | 30.5.708
SUF1INV3 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV3 | TmpStk2_Igbt_F | °C | 30.5.709
SUF1INV3 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV3 | TmpStk3_Igbt_F | °C | 30.5.710
SUF1INV3 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV3 | TmpStk1_Pcb_F | ?C | 30.5.711
SUF1INV3 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV3 | TmpStk2_Pcb_F | ?C | 30.5.712
SUF1INV3 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV3 | TmpStk3_Pcb_F | ?C | 30.5.713
SUF1INV3 | 106 | MV transformer pressure | SU F1 INV3 | PresTrf_F | "-" | 30.5.714
SUF1INV3 | 110 | Switching status of the DC load-break switch | SU F1 INV3 | DcSwStt | "-" | 30.5.715
SUINV3JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV3 | Dat_UpdCnt_1 | "-" | 30.5.716
SUINV3JB1 | 2 | DC current input 1 | SU F1 INV3 | DcMs_Amp_01 | A | 30.5.717
SUINV3JB1 | 3 | DC current input 2 | SU F1 INV3 | DcMs_Amp_02 | A | 30.5.718
SUINV3JB1 | 4 | DC current input 3 | SU F1 INV3 | DcMs_Amp_03 | A | 30.5.719
SUINV3JB1 | 5 | DC current input 4 | SU F1 INV3 | DcMs_Amp_04 | A | 30.5.720
SUINV3JB1 | 6 | DC current input 5 | SU F1 INV3 | DcMs_Amp_05 | A | 30.5.721
SUINV3JB1 | 7 | DC current input 6 | SU F1 INV3 | DcMs_Amp_06 | A | 30.5.722
SUINV3JB1 | 8 | DC current input 7 | SU F1 INV3 | DcMs_Amp_07 | A | 30.5.723
SUINV3JB1 | 9 | DC current input 8 | SU F1 INV3 | DcMs_Amp_08 | A | 30.5.724
SUINV3JB1 | 10 | DC current input 9 | SU F1 INV3 | DcMs_Amp_09 | A | 30.5.725
SUINV3JB1 | 11 | DC current input 10 | SU F1 INV3 | DcMs_Amp_10 | A | 30.5.726
SUINV3JB1 | 12 | DC current input 11 | SU F1 INV3 | DcMs_Amp_11 | A | 30.5.727
SUINV3JB1 | 13 | DC current input 12 | SU F1 INV3 | DcMs_Amp_12 | A | 30.5.728
SUINV3JB1 | 14 | DC current input 13 | SU F1 INV3 | DcMs_Amp_13 | A | 30.5.729
SUINV3JB1 | 15 | DC current input 14 | SU F1 INV3 | DcMs_Amp_14 | A | 30.5.730
SUINV3JB1 | 16 | DC current input 15 | SU F1 INV3 | DcMs_Amp_15 | A | 30.5.731
SUINV3JB1 | 17 | DC current input 16 | SU F1 INV3 | DcMs_Amp_16 | A | 30.5.732
SUINV3JB1 | 18 | DC current input 1 | SU F1 INV3 | DcMs_Amp_01_F | A | 30.5.733
SUINV3JB1 | 19 | DC current input 2 | SU F1 INV3 | DcMs_Amp_02_F | A | 30.5.734
SUINV3JB1 | 20 | DC current input 3 | SU F1 INV3 | DcMs_Amp_03_F | A | 30.5.735
SUINV3JB1 | 21 | DC current input 4 | SU F1 INV3 | DcMs_Amp_04_F | A | 30.5.736
SUINV3JB1 | 22 | DC current input 5 | SU F1 INV3 | DcMs_Amp_05_F | A | 30.5.737
SUINV3JB1 | 23 | DC current input 6 | SU F1 INV3 | DcMs_Amp_06_F | A | 30.5.738
SUINV3JB1 | 24 | DC current input 7 | SU F1 INV3 | DcMs_Amp_07_F | A | 30.5.739
SUINV3JB1 | 25 | DC current input 8 | SU F1 INV3 | DcMs_Amp_08_F | A | 30.5.740
SUINV3JB1 | 26 | DC current input 9 | SU F1 INV3 | DcMs_Amp_09_F | A | 30.5.741
SUINV3JB1 | 27 | DC current input 10 | SU F1 INV3 | DcMs_Amp_10_F | A | 30.5.742
SUINV3JB1 | 28 | DC current input 11 | SU F1 INV3 | DcMs_Amp_11_F | A | 30.5.743
SUINV3JB1 | 29 | DC current input 12 | SU F1 INV3 | DcMs_Amp_12_F | A | 30.5.744
SUINV3JB1 | 30 | DC current input 13 | SU F1 INV3 | DcMs_Amp_13_F | A | 30.5.745
SUINV3JB1 | 31 | DC current input 14 | SU F1 INV3 | DcMs_Amp_14_F | A | 30.5.746
SUINV3JB1 | 32 | DC current input 15 | SU F1 INV3 | DcMs_Amp_15_F | A | 30.5.747
SUINV3JB1 | 33 | DC current input 16 | SU F1 INV3 | DcMs_Amp_16_F | A | 30.5.748
SUINV3JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV3 | Dat_UpdCnt_1 | "-" | 30.5.749
SUINV3JB2 | 2 | DC current input 1 | SU F1 INV3 | DcMs_Amp_01 | A | 30.5.750
SUINV3JB2 | 3 | DC current input 2 | SU F1 INV3 | DcMs_Amp_02 | A | 30.5.751
SUINV3JB2 | 4 | DC current input 3 | SU F1 INV3 | DcMs_Amp_03 | A | 30.5.752
SUINV3JB2 | 5 | DC current input 4 | SU F1 INV3 | DcMs_Amp_04 | A | 30.5.753
SUINV3JB2 | 6 | DC current input 5 | SU F1 INV3 | DcMs_Amp_05 | A | 30.5.754
SUINV3JB2 | 7 | DC current input 6 | SU F1 INV3 | DcMs_Amp_06 | A | 30.5.755
SUINV3JB2 | 8 | DC current input 7 | SU F1 INV3 | DcMs_Amp_07 | A | 30.5.756
SUINV3JB2 | 9 | DC current input 8 | SU F1 INV3 | DcMs_Amp_08 | A | 30.5.757
SUINV3JB2 | 10 | DC current input 9 | SU F1 INV3 | DcMs_Amp_09 | A | 30.5.758
SUINV3JB2 | 11 | DC current input 10 | SU F1 INV3 | DcMs_Amp_10 | A | 30.5.759
SUINV3JB2 | 12 | DC current input 11 | SU F1 INV3 | DcMs_Amp_11 | A | 30.5.760
SUINV3JB2 | 13 | DC current input 12 | SU F1 INV3 | DcMs_Amp_12 | A | 30.5.761
SUINV3JB2 | 14 | DC current input 13 | SU F1 INV3 | DcMs_Amp_13 | A | 30.5.762
SUINV3JB2 | 15 | DC current input 14 | SU F1 INV3 | DcMs_Amp_14 | A | 30.5.763
SUINV3JB2 | 16 | DC current input 15 | SU F1 INV3 | DcMs_Amp_15 | A | 30.5.764
SUINV3JB2 | 17 | DC current input 16 | SU F1 INV3 | DcMs_Amp_16 | A | 30.5.765
SUINV3JB2 | 18 | DC current input 1 | SU F1 INV3 | DcMs_Amp_01_F | A | 30.5.766
SUINV3JB2 | 19 | DC current input 2 | SU F1 INV3 | DcMs_Amp_02_F | A | 30.5.767
SUINV3JB2 | 20 | DC current input 3 | SU F1 INV3 | DcMs_Amp_03_F | A | 30.5.768
SUINV3JB2 | 21 | DC current input 4 | SU F1 INV3 | DcMs_Amp_04_F | A | 30.5.769
SUINV3JB2 | 22 | DC current input 5 | SU F1 INV3 | DcMs_Amp_05_F | A | 30.5.770
SUINV3JB2 | 23 | DC current input 6 | SU F1 INV3 | DcMs_Amp_06_F | A | 30.5.771
SUINV3JB2 | 24 | DC current input 7 | SU F1 INV3 | DcMs_Amp_07_F | A | 30.5.772
SUINV3JB2 | 25 | DC current input 8 | SU F1 INV3 | DcMs_Amp_08_F | A | 30.5.773
SUINV3JB2 | 26 | DC current input 9 | SU F1 INV3 | DcMs_Amp_09_F | A | 30.5.774
SUINV3JB2 | 27 | DC current input 10 | SU F1 INV3 | DcMs_Amp_10_F | A | 30.5.775
SUINV3JB2 | 28 | DC current input 11 | SU F1 INV3 | DcMs_Amp_11_F | A | 30.5.776
SUINV3JB2 | 29 | DC current input 12 | SU F1 INV3 | DcMs_Amp_12_F | A | 30.5.777
SUINV3JB2 | 30 | DC current input 13 | SU F1 INV3 | DcMs_Amp_13_F | A | 30.5.778
SUINV3JB2 | 31 | DC current input 14 | SU F1 INV3 | DcMs_Amp_14_F | A | 30.5.779
SUINV3JB2 | 32 | DC current input 15 | SU F1 INV3 | DcMs_Amp_15_F | A | 30.5.780
SUINV3JB2 | 33 | DC current input 16 | SU F1 INV3 | DcMs_Amp_16_F | A | 30.5.781
SUF1INV4 | 1 | DC voltage DC plus to DC minus | SU F1 INV4 | DcMs_Vol | V | 30.5.782
SUF1INV4 | 2 | DC current inverter bridge 1 | SU F1 INV4 | DcMs_Amp_Stk1 | A | 30.5.783
SUF1INV4 | 3 | DC current inverter bridge 2 | SU F1 INV4 | DcMs_Amp_Stk2 | A | 30.5.784
SUF1INV4 | 4 | DC current inverter bridge 3 | SU F1 INV4 | DcMs_Amp_Stk3 | A | 30.5.785
SUF1INV4 | 5 | DC current, total | SU F1 INV4 | DcMs_TotAmp | A | 30.5.786
SUF1INV4 | 6 | DC power, total | SU F1 INV4 | DcMs_TotWatt | kW | 30.5.787
SUF1INV4 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV4 | InvMs_DclVol_Stk1 | V | 30.5.788
SUF1INV4 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV4 | InvMs_DclVol_Stk2 | V | 30.5.789
SUF1INV4 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV4 | InvMs_DclVol_Stk3 | V | 30.5.790
SUF1INV4 | 10 | AC current L1, total | SU F1 INV4 | InvMs_TotA_PhsA | A | 30.5.791
SUF1INV4 | 11 | AC current L2, total | SU F1 INV4 | InvMs_TotA_PhsB | A | 30.5.792
SUF1INV4 | 12 | AC current L3, total | SU F1 INV4 | InvMs_TotA_PhsC | A | 30.5.793
SUF1INV4 | 13 | Power factor (cos phi) | SU F1 INV4 | InvMs_PF | "-" | 30.5.794
SUF1INV4 | 14 | Apparent power, total | SU F1 INV4 | InvMs_TotVA | kVA | 30.5.795
SUF1INV4 | 15 | Active power, total | SU F1 INV4 | InvMs_TotW | kW | 30.5.796
SUF1INV4 | 16 | Reactive power, total | SU F1 INV4 | InvMs_TotVAr | kVAr | 30.5.797
SUF1INV4 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV4 | GriMs_V_PhsAB | V | 30.5.798
SUF1INV4 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV4 | GriMs_V_PhsBC | V | 30.5.799
SUF1INV4 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV4 | GriMs_V_PhsCA | V | 30.5.800
SUF1INV4 | 20 | Power frequency | SU F1 INV4 | GriMs_Hz | Hz | 30.5.801
SUF1INV4 | 21 | Temperature in the AC range | SU F1 INV4 | TmpCab_Acc | °C | 30.5.802
SUF1INV4 | 22 | Temperature in the DC range | SU F1 INV4 | TmpCab_Dcc | °C | 30.5.803
SUF1INV4 | 23 | Temperature in the electronics area | SU F1 INV4 | TmpCab_Rio | °C | 30.5.804
SUF1INV4 | 24 | Temperature in interior, maximum value | SU F1 INV4 | TmpCab_Max | °C | 30.5.805
SUF1INV4 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV4 | TmpStk_IgbtMax | °C | 30.5.806
SUF1INV4 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV4 | TmpStk_PcbMax | °C | 30.5.807
SUF1INV4 | 27 | Outside temperature | SU F1 INV4 | TmpExl | ?C | 30.5.808
SUF1INV4 | 28 | Temperature of the MV transformer | SU F1 INV4 | TmpTrf | °C | 30.5.809
SUF1INV4 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV4 | DcSw1Stt | "-" | 30.5.810
SUF1INV4 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV4 | DcSw2Stt | "-" | 30.5.811
SUF1INV4 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV4 | DcSw3Stt | "-" | 30.5.812
SUF1INV4 | 32 | Switching status of the AC circuit breaker | SU F1 INV4 | AcSwStt | "-" | 30.5.813
SUF1INV4 | 33 | Switching state of the capacitor contactor | SU F1 INV4 | CapacSwStt | "-" | 30.5.814
SUF1INV4 | 34 | Switching status of the pre-charging contactor | SU F1 INV4 | PrchrgSwStt | "-" | 30.5.815
SUF1INV4 | 35 | Feed-in hours | SU F1 INV4 | Cnt_TotFeedTm | "-" | 30.5.816
SUF1INV4 | 36 | Operating hours | SU F1 INV4 | Cnt_TotOpTm | "-" | 30.5.817
SUF1INV4 | 37 | DC energy drawn, total | SU F1 INV4 | Cnt_TotWatthIn | MWh | 30.5.818
SUF1INV4 | 38 | AC energy fed in, total | SU F1 INV4 | Cnt_TotWhOut | MWh | 30.5.819
SUF1INV4 | 39 | DC energy drawn that day | SU F1 INV4 | Cnt_WatthIn | MWh | 30.5.820
SUF1INV4 | 40 | AC energy fed in that day | SU F1 INV4 | Cnt_WhOut | MWh | 30.5.821
SUF1INV4 | 41 | Operating hours of the interior fan 1 | SU F1 INV4 | Cnt_FanCab1Tm | "-" | 30.5.822
SUF1INV4 | 42 | Operating hours of the interior fan 2 | SU F1 INV4 | Cnt_FanCab2Tm | "-" | 30.5.823
SUF1INV4 | 43 | Operating hours of the inverter bridge fan | SU F1 INV4 | Cnt_FanStkTm | "-" | 30.5.824
SUF1INV4 | 44 | Operating hours of the internal heating element | SU F1 INV4 | Cnt_HtCabTm | "-" | 30.5.825
SUF1INV4 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV4 | Cnt_HtLoExlTmpTm | "-" | 30.5.826
SUF1INV4 | 46 | Error location of the present error | SU F1 INV4 | ErrLcn | "-" | 30.5.827
SUF1INV4 | 47 | Error status of the inverter | SU F1 INV4 | ErrStt | "-" | 30.5.828
SUF1INV4 | 48 | Error number of the present error | SU F1 INV4 | ErrNo | "-" | 30.5.829
SUF1INV4 | 49 | Operating state of the inverter | SU F1 INV4 | OpStt | "-" | 30.5.830
SUF1INV4 | 50 | Switch status of the start-stop key switch | SU F1 INV4 | Rio_KeySw | "-" | 30.5.831
SUF1INV4 | 51 | Waiting time for grid connection | SU F1 INV4 | WaitGriTm | s | 30.5.832
SUF1INV4 | 52 | Inverter serial number | SU F1 INV4 | DevInf_SerNo | "-" | 30.5.833
SUF1INV4 | 53 | Switching status of the GFDI | SU F1 INV4 | GfdiSwStt | "-" | 30.5.834
SUF1INV4 | 54 | Active power, setpoint | SU F1 INV4 | WSpt | kW | 30.5.835
SUF1INV4 | 55 | Maximum apparent power, setpoint | SU F1 INV4 | VAMaxSpt | kVA | 30.5.836
SUF1INV4 | 56 | Reactive power, setpoint | SU F1 INV4 | VArSpt | kVAr | 30.5.837
SUF1INV4 | 57 | Power factor cos (phi), setpoint | SU F1 INV4 | PFSpt | "-" | 30.5.838
SUF1INV4 | 58 | Fast stop hermetic protection, pressure | SU F1 INV4 | TrfPro_Pres | "-" | 30.5.839
SUF1INV4 | 59 | Fast stop hermetic protection, temperature | SU F1 INV4 | TrfPro_TmpTrp | "-" | 30.5.840
SUF1INV4 | 60 | Hermetic protection, gas fill level | SU F1 INV4 | TrfPro_GasOilLev | "-" | 30.5.841
SUF1INV4 | 61 | Hermetic pressure, temperature warning | SU F1 INV4 | TrfPro_TmpWrn | "-" | 30.5.842
SUF1INV4 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV4 | TmpStk1_Igbt | °C | 30.5.843
SUF1INV4 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV4 | TmpStk2_Igbt | °C | 30.5.844
SUF1INV4 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV4 | TmpStk3_Igbt | °C | 30.5.845
SUF1INV4 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV4 | TmpStk1_Pcb | ?C | 30.5.846
SUF1INV4 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV4 | TmpStk2_Pcb | ?C | 30.5.847
SUF1INV4 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV4 | TmpStk3_Pcb | ?C | 30.5.848
SUF1INV4 | 68 | AC Energy Fed in the previous Day | SU F1 INV4 | Cnt_YstdWhOut | MWh | 30.5.849
SUF1INV4 | 69 | CPU running time since system start | SU F1 INV4 | Cpu1UpTime | s | 30.5.850
SUF1INV4 | 70 | Insulation resistance | SU F1 INV4 | PvGnd_RisIso | kOhm | 30.5.851
SUF1INV4 | 71 | MV transformer pressure | SU F1 INV4 | PresTrf | "-" | 30.5.852
SUF1INV4 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV4 | PresTrf_ErrStt | "-" | 30.5.853
SUF1INV4 | 73 | DC voltage DC plus to DC minus | SU F1 INV4 | DcMs_Vol_F | V | 30.5.854
SUF1INV4 | 74 | DC current inverter bridge 1 | SU F1 INV4 | DcMs_Amp_Stk1_F | A | 30.5.855
SUF1INV4 | 75 | DC current inverter bridge 2 | SU F1 INV4 | DcMs_Amp_Stk2_F | A | 30.5.856
SUF1INV4 | 76 | DC current inverter bridge 3 | SU F1 INV4 | DcMs_Amp_Stk3_F | A | 30.5.857
SUF1INV4 | 77 | DC current, total | SU F1 INV4 | DcMs_TotAmp_F | A | 30.5.858
SUF1INV4 | 78 | DC power, total | SU F1 INV4 | DcMs_TotWatt_F | kW | 30.5.859
SUF1INV4 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV4 | InvMs_DclVol_Stk1_F | V | 30.5.860
SUF1INV4 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV4 | InvMs_DclVol_Stk2_F | V | 30.5.861
SUF1INV4 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV4 | InvMs_DclVol_Stk3_F | V | 30.5.862
SUF1INV4 | 82 | AC current L1, total | SU F1 INV4 | InvMs_TotA_PhsA_F | A | 30.5.863
SUF1INV4 | 83 | AC current L2, total | SU F1 INV4 | InvMs_TotA_PhsB_F | A | 30.5.864
SUF1INV4 | 84 | AC current L3, total | SU F1 INV4 | InvMs_TotA_PhsC_F | A | 30.5.865
SUF1INV4 | 85 | Power factor (cos phi) | SU F1 INV4 | InvMs_PF_F | "-" | 30.5.866
SUF1INV4 | 86 | Active power, total | SU F1 INV4 | InvMs_TotW_F | kW | 30.5.867
SUF1INV4 | 87 | Reactive power, total | SU F1 INV4 | InvMs_TotVAr_F | kVAr | 30.5.868
SUF1INV4 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV4 | GriMs_V_PhsAB_F | V | 30.5.869
SUF1INV4 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV4 | GriMs_V_PhsBC_F | V | 30.5.870
SUF1INV4 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV4 | GriMs_V_PhsCA_F | V | 30.5.871
SUF1INV4 | 91 | Power frequency | SU F1 INV4 | GriMs_Hz_F | Hz | 30.5.872
SUF1INV4 | 92 | Temperature in the AC range | SU F1 INV4 | TmpCab_Acc_F | °C | 30.5.873
SUF1INV4 | 93 | Temperature in the DC range | SU F1 INV4 | TmpCab_Dcc_F | °C | 30.5.874
SUF1INV4 | 94 | Temperature in the electronics area | SU F1 INV4 | TmpCab_Rio_F | °C | 30.5.875
SUF1INV4 | 95 | Temperature in interior, maximum value | SU F1 INV4 | TmpCab_Max_F | °C | 30.5.876
SUF1INV4 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV4 | TmpStk_IgbtMax_F | °C | 30.5.877
SUF1INV4 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV4 | TmpStk_PcbMax_F | °C | 30.5.878
SUF1INV4 | 98 | Outside temperature | SU F1 INV4 | TmpExl_F | ?C | 30.5.879
SUF1INV4 | 99 | Temperature of the MV transformer | SU F1 INV4 | TmpTrf_F | °C | 30.5.880
SUF1INV4 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV4 | TmpStk1_Igbt_F | °C | 30.5.881
SUF1INV4 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV4 | TmpStk2_Igbt_F | °C | 30.5.882
SUF1INV4 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV4 | TmpStk3_Igbt_F | °C | 30.5.883
SUF1INV4 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV4 | TmpStk1_Pcb_F | ?C | 30.5.884
SUF1INV4 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV4 | TmpStk2_Pcb_F | ?C | 30.5.885
SUF1INV4 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV4 | TmpStk3_Pcb_F | ?C | 30.5.886
SUF1INV4 | 106 | MV transformer pressure | SU F1 INV4 | PresTrf_F | "-" | 30.5.887
SUF1INV4 | 110 | Switching status of the DC load-break switch | SU F1 INV4 | DcSwStt | "-" | 30.5.888
SUINV4JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV4 | Dat_UpdCnt_1 | "-" | 30.5.889
SUINV4JB1 | 2 | DC current input 1 | SU F1 INV4 | DcMs_Amp_01 | A | 30.5.890
SUINV4JB1 | 3 | DC current input 2 | SU F1 INV4 | DcMs_Amp_02 | A | 30.5.891
SUINV4JB1 | 4 | DC current input 3 | SU F1 INV4 | DcMs_Amp_03 | A | 30.5.892
SUINV4JB1 | 5 | DC current input 4 | SU F1 INV4 | DcMs_Amp_04 | A | 30.5.893
SUINV4JB1 | 6 | DC current input 5 | SU F1 INV4 | DcMs_Amp_05 | A | 30.5.894
SUINV4JB1 | 7 | DC current input 6 | SU F1 INV4 | DcMs_Amp_06 | A | 30.5.895
SUINV4JB1 | 8 | DC current input 7 | SU F1 INV4 | DcMs_Amp_07 | A | 30.5.896
SUINV4JB1 | 9 | DC current input 8 | SU F1 INV4 | DcMs_Amp_08 | A | 30.5.897
SUINV4JB1 | 10 | DC current input 9 | SU F1 INV4 | DcMs_Amp_09 | A | 30.5.898
SUINV4JB1 | 11 | DC current input 10 | SU F1 INV4 | DcMs_Amp_10 | A | 30.5.899
SUINV4JB1 | 12 | DC current input 11 | SU F1 INV4 | DcMs_Amp_11 | A | 30.5.900
SUINV4JB1 | 13 | DC current input 12 | SU F1 INV4 | DcMs_Amp_12 | A | 30.5.901
SUINV4JB1 | 14 | DC current input 13 | SU F1 INV4 | DcMs_Amp_13 | A | 30.5.902
SUINV4JB1 | 15 | DC current input 14 | SU F1 INV4 | DcMs_Amp_14 | A | 30.5.903
SUINV4JB1 | 16 | DC current input 15 | SU F1 INV4 | DcMs_Amp_15 | A | 30.5.904
SUINV4JB1 | 17 | DC current input 16 | SU F1 INV4 | DcMs_Amp_16 | A | 30.5.905
SUINV4JB1 | 18 | DC current input 1 | SU F1 INV4 | DcMs_Amp_01_F | A | 30.5.906
SUINV4JB1 | 19 | DC current input 2 | SU F1 INV4 | DcMs_Amp_02_F | A | 30.5.907
SUINV4JB1 | 20 | DC current input 3 | SU F1 INV4 | DcMs_Amp_03_F | A | 30.5.908
SUINV4JB1 | 21 | DC current input 4 | SU F1 INV4 | DcMs_Amp_04_F | A | 30.5.909
SUINV4JB1 | 22 | DC current input 5 | SU F1 INV4 | DcMs_Amp_05_F | A | 30.5.910
SUINV4JB1 | 23 | DC current input 6 | SU F1 INV4 | DcMs_Amp_06_F | A | 30.5.911
SUINV4JB1 | 24 | DC current input 7 | SU F1 INV4 | DcMs_Amp_07_F | A | 30.5.912
SUINV4JB1 | 25 | DC current input 8 | SU F1 INV4 | DcMs_Amp_08_F | A | 30.5.913
SUINV4JB1 | 26 | DC current input 9 | SU F1 INV4 | DcMs_Amp_09_F | A | 30.5.914
SUINV4JB1 | 27 | DC current input 10 | SU F1 INV4 | DcMs_Amp_10_F | A | 30.5.915
SUINV4JB1 | 28 | DC current input 11 | SU F1 INV4 | DcMs_Amp_11_F | A | 30.5.916
SUINV4JB1 | 29 | DC current input 12 | SU F1 INV4 | DcMs_Amp_12_F | A | 30.5.917
SUINV4JB1 | 30 | DC current input 13 | SU F1 INV4 | DcMs_Amp_13_F | A | 30.5.918
SUINV4JB1 | 31 | DC current input 14 | SU F1 INV4 | DcMs_Amp_14_F | A | 30.5.919
SUINV4JB1 | 32 | DC current input 15 | SU F1 INV4 | DcMs_Amp_15_F | A | 30.5.920
SUINV4JB1 | 33 | DC current input 16 | SU F1 INV4 | DcMs_Amp_16_F | A | 30.5.921
SUINV4JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV4 | Dat_UpdCnt_1 | "-" | 30.5.922
SUINV4JB2 | 2 | DC current input 1 | SU F1 INV4 | DcMs_Amp_01 | A | 30.5.923
SUINV4JB2 | 3 | DC current input 2 | SU F1 INV4 | DcMs_Amp_02 | A | 30.5.924
SUINV4JB2 | 4 | DC current input 3 | SU F1 INV4 | DcMs_Amp_03 | A | 30.5.925
SUINV4JB2 | 5 | DC current input 4 | SU F1 INV4 | DcMs_Amp_04 | A | 30.5.926
SUINV4JB2 | 6 | DC current input 5 | SU F1 INV4 | DcMs_Amp_05 | A | 30.5.927
SUINV4JB2 | 7 | DC current input 6 | SU F1 INV4 | DcMs_Amp_06 | A | 30.5.928
SUINV4JB2 | 8 | DC current input 7 | SU F1 INV4 | DcMs_Amp_07 | A | 30.5.929
SUINV4JB2 | 9 | DC current input 8 | SU F1 INV4 | DcMs_Amp_08 | A | 30.5.930
SUINV4JB2 | 10 | DC current input 9 | SU F1 INV4 | DcMs_Amp_09 | A | 30.5.931
SUINV4JB2 | 11 | DC current input 10 | SU F1 INV4 | DcMs_Amp_10 | A | 30.5.932
SUINV4JB2 | 12 | DC current input 11 | SU F1 INV4 | DcMs_Amp_11 | A | 30.5.933
SUINV4JB2 | 13 | DC current input 12 | SU F1 INV4 | DcMs_Amp_12 | A | 30.5.934
SUINV4JB2 | 14 | DC current input 13 | SU F1 INV4 | DcMs_Amp_13 | A | 30.5.935
SUINV4JB2 | 15 | DC current input 14 | SU F1 INV4 | DcMs_Amp_14 | A | 30.5.936
SUINV4JB2 | 16 | DC current input 15 | SU F1 INV4 | DcMs_Amp_15 | A | 30.5.937
SUINV4JB2 | 17 | DC current input 16 | SU F1 INV4 | DcMs_Amp_16 | A | 30.5.938
SUINV4JB2 | 18 | DC current input 1 | SU F1 INV4 | DcMs_Amp_01_F | A | 30.5.939
SUINV4JB2 | 19 | DC current input 2 | SU F1 INV4 | DcMs_Amp_02_F | A | 30.5.940
SUINV4JB2 | 20 | DC current input 3 | SU F1 INV4 | DcMs_Amp_03_F | A | 30.5.941
SUINV4JB2 | 21 | DC current input 4 | SU F1 INV4 | DcMs_Amp_04_F | A | 30.5.942
SUINV4JB2 | 22 | DC current input 5 | SU F1 INV4 | DcMs_Amp_05_F | A | 30.5.943
SUINV4JB2 | 23 | DC current input 6 | SU F1 INV4 | DcMs_Amp_06_F | A | 30.5.944
SUINV4JB2 | 24 | DC current input 7 | SU F1 INV4 | DcMs_Amp_07_F | A | 30.5.945
SUINV4JB2 | 25 | DC current input 8 | SU F1 INV4 | DcMs_Amp_08_F | A | 30.5.946
SUINV4JB2 | 26 | DC current input 9 | SU F1 INV4 | DcMs_Amp_09_F | A | 30.5.947
SUINV4JB2 | 27 | DC current input 10 | SU F1 INV4 | DcMs_Amp_10_F | A | 30.5.948
SUINV4JB2 | 28 | DC current input 11 | SU F1 INV4 | DcMs_Amp_11_F | A | 30.5.949
SUINV4JB2 | 29 | DC current input 12 | SU F1 INV4 | DcMs_Amp_12_F | A | 30.5.950
SUINV4JB2 | 30 | DC current input 13 | SU F1 INV4 | DcMs_Amp_13_F | A | 30.5.951
SUINV4JB2 | 31 | DC current input 14 | SU F1 INV4 | DcMs_Amp_14_F | A | 30.5.952
SUINV4JB2 | 32 | DC current input 15 | SU F1 INV4 | DcMs_Amp_15_F | A | 30.5.953
SUINV4JB2 | 33 | DC current input 16 | SU F1 INV4 | DcMs_Amp_16_F | A | 30.5.954
SUF1INV5 | 1 | DC voltage DC plus to DC minus | SU F1 INV5 | DcMs_Vol | V | 30.5.955
SUF1INV5 | 2 | DC current inverter bridge 1 | SU F1 INV5 | DcMs_Amp_Stk1 | A | 30.5.956
SUF1INV5 | 3 | DC current inverter bridge 2 | SU F1 INV5 | DcMs_Amp_Stk2 | A | 30.5.957
SUF1INV5 | 4 | DC current inverter bridge 3 | SU F1 INV5 | DcMs_Amp_Stk3 | A | 30.5.958
SUF1INV5 | 5 | DC current, total | SU F1 INV5 | DcMs_TotAmp | A | 30.5.959
SUF1INV5 | 6 | DC power, total | SU F1 INV5 | DcMs_TotWatt | kW | 30.5.960
SUF1INV5 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV5 | InvMs_DclVol_Stk1 | V | 30.5.961
SUF1INV5 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV5 | InvMs_DclVol_Stk2 | V | 30.5.962
SUF1INV5 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV5 | InvMs_DclVol_Stk3 | V | 30.5.963
SUF1INV5 | 10 | AC current L1, total | SU F1 INV5 | InvMs_TotA_PhsA | A | 30.5.964
SUF1INV5 | 11 | AC current L2, total | SU F1 INV5 | InvMs_TotA_PhsB | A | 30.5.965
SUF1INV5 | 12 | AC current L3, total | SU F1 INV5 | InvMs_TotA_PhsC | A | 30.5.966
SUF1INV5 | 13 | Power factor (cos phi) | SU F1 INV5 | InvMs_PF | "-" | 30.5.967
SUF1INV5 | 14 | Apparent power, total | SU F1 INV5 | InvMs_TotVA | kVA | 30.5.968
SUF1INV5 | 15 | Active power, total | SU F1 INV5 | InvMs_TotW | kW | 30.5.969
SUF1INV5 | 16 | Reactive power, total | SU F1 INV5 | InvMs_TotVAr | kVAr | 30.5.970
SUF1INV5 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV5 | GriMs_V_PhsAB | V | 30.5.971
SUF1INV5 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV5 | GriMs_V_PhsBC | V | 30.5.972
SUF1INV5 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV5 | GriMs_V_PhsCA | V | 30.5.973
SUF1INV5 | 20 | Power frequency | SU F1 INV5 | GriMs_Hz | Hz | 30.5.974
SUF1INV5 | 21 | Temperature in the AC range | SU F1 INV5 | TmpCab_Acc | °C | 30.5.975
SUF1INV5 | 22 | Temperature in the DC range | SU F1 INV5 | TmpCab_Dcc | °C | 30.5.976
SUF1INV5 | 23 | Temperature in the electronics area | SU F1 INV5 | TmpCab_Rio | °C | 30.5.977
SUF1INV5 | 24 | Temperature in interior, maximum value | SU F1 INV5 | TmpCab_Max | °C | 30.5.978
SUF1INV5 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV5 | TmpStk_IgbtMax | °C | 30.5.979
SUF1INV5 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV5 | TmpStk_PcbMax | °C | 30.5.980
SUF1INV5 | 27 | Outside temperature | SU F1 INV5 | TmpExl | ?C | 30.5.981
SUF1INV5 | 28 | Temperature of the MV transformer | SU F1 INV5 | TmpTrf | °C | 30.5.982
SUF1INV5 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV5 | DcSw1Stt | "-" | 30.5.983
SUF1INV5 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV5 | DcSw2Stt | "-" | 30.5.984
SUF1INV5 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV5 | DcSw3Stt | "-" | 30.5.985
SUF1INV5 | 32 | Switching status of the AC circuit breaker | SU F1 INV5 | AcSwStt | "-" | 30.5.986
SUF1INV5 | 33 | Switching state of the capacitor contactor | SU F1 INV5 | CapacSwStt | "-" | 30.5.987
SUF1INV5 | 34 | Switching status of the pre-charging contactor | SU F1 INV5 | PrchrgSwStt | "-" | 30.5.988
SUF1INV5 | 35 | Feed-in hours | SU F1 INV5 | Cnt_TotFeedTm | "-" | 30.5.989
SUF1INV5 | 36 | Operating hours | SU F1 INV5 | Cnt_TotOpTm | "-" | 30.5.990
SUF1INV5 | 37 | DC energy drawn, total | SU F1 INV5 | Cnt_TotWatthIn | MWh | 30.5.991
SUF1INV5 | 38 | AC energy fed in, total | SU F1 INV5 | Cnt_TotWhOut | MWh | 30.5.992
SUF1INV5 | 39 | DC energy drawn that day | SU F1 INV5 | Cnt_WatthIn | MWh | 30.5.993
SUF1INV5 | 40 | AC energy fed in that day | SU F1 INV5 | Cnt_WhOut | MWh | 30.5.994
SUF1INV5 | 41 | Operating hours of the interior fan 1 | SU F1 INV5 | Cnt_FanCab1Tm | "-" | 30.5.995
SUF1INV5 | 42 | Operating hours of the interior fan 2 | SU F1 INV5 | Cnt_FanCab2Tm | "-" | 30.5.996
SUF1INV5 | 43 | Operating hours of the inverter bridge fan | SU F1 INV5 | Cnt_FanStkTm | "-" | 30.5.997
SUF1INV5 | 44 | Operating hours of the internal heating element | SU F1 INV5 | Cnt_HtCabTm | "-" | 30.5.998
SUF1INV5 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV5 | Cnt_HtLoExlTmpTm | "-" | 30.5.999
SUF1INV5 | 46 | Error location of the present error | SU F1 INV5 | ErrLcn | "-" | 30.5.1000
SUF1INV5 | 47 | Error status of the inverter | SU F1 INV5 | ErrStt | "-" | 30.5.1001
SUF1INV5 | 48 | Error number of the present error | SU F1 INV5 | ErrNo | "-" | 30.5.1002
SUF1INV5 | 49 | Operating state of the inverter | SU F1 INV5 | OpStt | "-" | 30.5.1003
SUF1INV5 | 50 | Switch status of the start-stop key switch | SU F1 INV5 | Rio_KeySw | "-" | 30.5.1004
SUF1INV5 | 51 | Waiting time for grid connection | SU F1 INV5 | WaitGriTm | s | 30.5.1005
SUF1INV5 | 52 | Inverter serial number | SU F1 INV5 | DevInf_SerNo | "-" | 30.5.1006
SUF1INV5 | 53 | Switching status of the GFDI | SU F1 INV5 | GfdiSwStt | "-" | 30.5.1007
SUF1INV5 | 54 | Active power, setpoint | SU F1 INV5 | WSpt | kW | 30.5.1008
SUF1INV5 | 55 | Maximum apparent power, setpoint | SU F1 INV5 | VAMaxSpt | kVA | 30.5.1009
SUF1INV5 | 56 | Reactive power, setpoint | SU F1 INV5 | VArSpt | kVAr | 30.5.1010
SUF1INV5 | 57 | Power factor cos (phi), setpoint | SU F1 INV5 | PFSpt | "-" | 30.5.1011
SUF1INV5 | 58 | Fast stop hermetic protection, pressure | SU F1 INV5 | TrfPro_Pres | "-" | 30.5.1012
SUF1INV5 | 59 | Fast stop hermetic protection, temperature | SU F1 INV5 | TrfPro_TmpTrp | "-" | 30.5.1013
SUF1INV5 | 60 | Hermetic protection, gas fill level | SU F1 INV5 | TrfPro_GasOilLev | "-" | 30.5.1014
SUF1INV5 | 61 | Hermetic pressure, temperature warning | SU F1 INV5 | TrfPro_TmpWrn | "-" | 30.5.1015
SUF1INV5 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV5 | TmpStk1_Igbt | °C | 30.5.1016
SUF1INV5 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV5 | TmpStk2_Igbt | °C | 30.5.1017
SUF1INV5 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV5 | TmpStk3_Igbt | °C | 30.5.1018
SUF1INV5 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV5 | TmpStk1_Pcb | ?C | 30.5.1019
SUF1INV5 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV5 | TmpStk2_Pcb | ?C | 30.5.1020
SUF1INV5 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV5 | TmpStk3_Pcb | ?C | 30.5.1021
SUF1INV5 | 68 | AC Energy Fed in the previous Day | SU F1 INV5 | Cnt_YstdWhOut | MWh | 30.5.1022
SUF1INV5 | 69 | CPU running time since system start | SU F1 INV5 | Cpu1UpTime | s | 30.5.1023
SUF1INV5 | 70 | Insulation resistance | SU F1 INV5 | PvGnd_RisIso | kOhm | 30.5.1024
SUF1INV5 | 71 | MV transformer pressure | SU F1 INV5 | PresTrf | "-" | 30.5.1025
SUF1INV5 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV5 | PresTrf_ErrStt | "-" | 30.5.1026
SUF1INV5 | 73 | DC voltage DC plus to DC minus | SU F1 INV5 | DcMs_Vol_F | V | 30.5.1027
SUF1INV5 | 74 | DC current inverter bridge 1 | SU F1 INV5 | DcMs_Amp_Stk1_F | A | 30.5.1028
SUF1INV5 | 75 | DC current inverter bridge 2 | SU F1 INV5 | DcMs_Amp_Stk2_F | A | 30.5.1029
SUF1INV5 | 76 | DC current inverter bridge 3 | SU F1 INV5 | DcMs_Amp_Stk3_F | A | 30.5.1030
SUF1INV5 | 77 | DC current, total | SU F1 INV5 | DcMs_TotAmp_F | A | 30.5.1031
SUF1INV5 | 78 | DC power, total | SU F1 INV5 | DcMs_TotWatt_F | kW | 30.5.1032
SUF1INV5 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV5 | InvMs_DclVol_Stk1_F | V | 30.5.1033
SUF1INV5 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV5 | InvMs_DclVol_Stk2_F | V | 30.5.1034
SUF1INV5 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV5 | InvMs_DclVol_Stk3_F | V | 30.5.1035
SUF1INV5 | 82 | AC current L1, total | SU F1 INV5 | InvMs_TotA_PhsA_F | A | 30.5.1036
SUF1INV5 | 83 | AC current L2, total | SU F1 INV5 | InvMs_TotA_PhsB_F | A | 30.5.1037
SUF1INV5 | 84 | AC current L3, total | SU F1 INV5 | InvMs_TotA_PhsC_F | A | 30.5.1038
SUF1INV5 | 85 | Power factor (cos phi) | SU F1 INV5 | InvMs_PF_F | "-" | 30.5.1039
SUF1INV5 | 86 | Active power, total | SU F1 INV5 | InvMs_TotW_F | kW | 30.5.1040
SUF1INV5 | 87 | Reactive power, total | SU F1 INV5 | InvMs_TotVAr_F | kVAr | 30.5.1041
SUF1INV5 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV5 | GriMs_V_PhsAB_F | V | 30.5.1042
SUF1INV5 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV5 | GriMs_V_PhsBC_F | V | 30.5.1043
SUF1INV5 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV5 | GriMs_V_PhsCA_F | V | 30.5.1044
SUF1INV5 | 91 | Power frequency | SU F1 INV5 | GriMs_Hz_F | Hz | 30.5.1045
SUF1INV5 | 92 | Temperature in the AC range | SU F1 INV5 | TmpCab_Acc_F | °C | 30.5.1046
SUF1INV5 | 93 | Temperature in the DC range | SU F1 INV5 | TmpCab_Dcc_F | °C | 30.5.1047
SUF1INV5 | 94 | Temperature in the electronics area | SU F1 INV5 | TmpCab_Rio_F | °C | 30.5.1048
SUF1INV5 | 95 | Temperature in interior, maximum value | SU F1 INV5 | TmpCab_Max_F | °C | 30.5.1049
SUF1INV5 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV5 | TmpStk_IgbtMax_F | °C | 30.5.1050
SUF1INV5 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV5 | TmpStk_PcbMax_F | °C | 30.5.1051
SUF1INV5 | 98 | Outside temperature | SU F1 INV5 | TmpExl_F | ?C | 30.5.1052
SUF1INV5 | 99 | Temperature of the MV transformer | SU F1 INV5 | TmpTrf_F | °C | 30.5.1053
SUF1INV5 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV5 | TmpStk1_Igbt_F | °C | 30.5.1054
SUF1INV5 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV5 | TmpStk2_Igbt_F | °C | 30.5.1055
SUF1INV5 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV5 | TmpStk3_Igbt_F | °C | 30.5.1056
SUF1INV5 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV5 | TmpStk1_Pcb_F | ?C | 30.5.1057
SUF1INV5 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV5 | TmpStk2_Pcb_F | ?C | 30.5.1058
SUF1INV5 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV5 | TmpStk3_Pcb_F | ?C | 30.5.1059
SUF1INV5 | 106 | MV transformer pressure | SU F1 INV5 | PresTrf_F | "-" | 30.5.1060
SUF1INV5 | 110 | Switching status of the DC load-break switch | SU F1 INV5 | DcSwStt | "-" | 30.5.1061
SUINV5JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV5 | Dat_UpdCnt_1 | "-" | 30.5.1062
SUINV5JB1 | 2 | DC current input 1 | SU F1 INV5 | DcMs_Amp_01 | A | 30.5.1063
SUINV5JB1 | 3 | DC current input 2 | SU F1 INV5 | DcMs_Amp_02 | A | 30.5.1064
SUINV5JB1 | 4 | DC current input 3 | SU F1 INV5 | DcMs_Amp_03 | A | 30.5.1065
SUINV5JB1 | 5 | DC current input 4 | SU F1 INV5 | DcMs_Amp_04 | A | 30.5.1066
SUINV5JB1 | 6 | DC current input 5 | SU F1 INV5 | DcMs_Amp_05 | A | 30.5.1067
SUINV5JB1 | 7 | DC current input 6 | SU F1 INV5 | DcMs_Amp_06 | A | 30.5.1068
SUINV5JB1 | 8 | DC current input 7 | SU F1 INV5 | DcMs_Amp_07 | A | 30.5.1069
SUINV5JB1 | 9 | DC current input 8 | SU F1 INV5 | DcMs_Amp_08 | A | 30.5.1070
SUINV5JB1 | 10 | DC current input 9 | SU F1 INV5 | DcMs_Amp_09 | A | 30.5.1071
SUINV5JB1 | 11 | DC current input 10 | SU F1 INV5 | DcMs_Amp_10 | A | 30.5.1072
SUINV5JB1 | 12 | DC current input 11 | SU F1 INV5 | DcMs_Amp_11 | A | 30.5.1073
SUINV5JB1 | 13 | DC current input 12 | SU F1 INV5 | DcMs_Amp_12 | A | 30.5.1074
SUINV5JB1 | 14 | DC current input 13 | SU F1 INV5 | DcMs_Amp_13 | A | 30.5.1075
SUINV5JB1 | 15 | DC current input 14 | SU F1 INV5 | DcMs_Amp_14 | A | 30.5.1076
SUINV5JB1 | 16 | DC current input 15 | SU F1 INV5 | DcMs_Amp_15 | A | 30.5.1077
SUINV5JB1 | 17 | DC current input 16 | SU F1 INV5 | DcMs_Amp_16 | A | 30.5.1078
SUINV5JB1 | 18 | DC current input 1 | SU F1 INV5 | DcMs_Amp_01_F | A | 30.5.1079
SUINV5JB1 | 19 | DC current input 2 | SU F1 INV5 | DcMs_Amp_02_F | A | 30.5.1080
SUINV5JB1 | 20 | DC current input 3 | SU F1 INV5 | DcMs_Amp_03_F | A | 30.5.1081
SUINV5JB1 | 21 | DC current input 4 | SU F1 INV5 | DcMs_Amp_04_F | A | 30.5.1082
SUINV5JB1 | 22 | DC current input 5 | SU F1 INV5 | DcMs_Amp_05_F | A | 30.5.1083
SUINV5JB1 | 23 | DC current input 6 | SU F1 INV5 | DcMs_Amp_06_F | A | 30.5.1084
SUINV5JB1 | 24 | DC current input 7 | SU F1 INV5 | DcMs_Amp_07_F | A | 30.5.1085
SUINV5JB1 | 25 | DC current input 8 | SU F1 INV5 | DcMs_Amp_08_F | A | 30.5.1086
SUINV5JB1 | 26 | DC current input 9 | SU F1 INV5 | DcMs_Amp_09_F | A | 30.5.1087
SUINV5JB1 | 27 | DC current input 10 | SU F1 INV5 | DcMs_Amp_10_F | A | 30.5.1088
SUINV5JB1 | 28 | DC current input 11 | SU F1 INV5 | DcMs_Amp_11_F | A | 30.5.1089
SUINV5JB1 | 29 | DC current input 12 | SU F1 INV5 | DcMs_Amp_12_F | A | 30.5.1090
SUINV5JB1 | 30 | DC current input 13 | SU F1 INV5 | DcMs_Amp_13_F | A | 30.5.1091
SUINV5JB1 | 31 | DC current input 14 | SU F1 INV5 | DcMs_Amp_14_F | A | 30.5.1092
SUINV5JB1 | 32 | DC current input 15 | SU F1 INV5 | DcMs_Amp_15_F | A | 30.5.1093
SUINV5JB1 | 33 | DC current input 16 | SU F1 INV5 | DcMs_Amp_16_F | A | 30.5.1094
SUINV5JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV5 | Dat_UpdCnt_1 | "-" | 30.5.1095
SUINV5JB2 | 2 | DC current input 1 | SU F1 INV5 | DcMs_Amp_01 | A | 30.5.1096
SUINV5JB2 | 3 | DC current input 2 | SU F1 INV5 | DcMs_Amp_02 | A | 30.5.1097
SUINV5JB2 | 4 | DC current input 3 | SU F1 INV5 | DcMs_Amp_03 | A | 30.5.1098
SUINV5JB2 | 5 | DC current input 4 | SU F1 INV5 | DcMs_Amp_04 | A | 30.5.1099
SUINV5JB2 | 6 | DC current input 5 | SU F1 INV5 | DcMs_Amp_05 | A | 30.5.1100
SUINV5JB2 | 7 | DC current input 6 | SU F1 INV5 | DcMs_Amp_06 | A | 30.5.1101
SUINV5JB2 | 8 | DC current input 7 | SU F1 INV5 | DcMs_Amp_07 | A | 30.5.1102
SUINV5JB2 | 9 | DC current input 8 | SU F1 INV5 | DcMs_Amp_08 | A | 30.5.1103
SUINV5JB2 | 10 | DC current input 9 | SU F1 INV5 | DcMs_Amp_09 | A | 30.5.1104
SUINV5JB2 | 11 | DC current input 10 | SU F1 INV5 | DcMs_Amp_10 | A | 30.5.1105
SUINV5JB2 | 12 | DC current input 11 | SU F1 INV5 | DcMs_Amp_11 | A | 30.5.1106
SUINV5JB2 | 13 | DC current input 12 | SU F1 INV5 | DcMs_Amp_12 | A | 30.5.1107
SUINV5JB2 | 14 | DC current input 13 | SU F1 INV5 | DcMs_Amp_13 | A | 30.5.1108
SUINV5JB2 | 15 | DC current input 14 | SU F1 INV5 | DcMs_Amp_14 | A | 30.5.1109
SUINV5JB2 | 16 | DC current input 15 | SU F1 INV5 | DcMs_Amp_15 | A | 30.5.1110
SUINV5JB2 | 17 | DC current input 16 | SU F1 INV5 | DcMs_Amp_16 | A | 30.5.1111
SUINV5JB2 | 18 | DC current input 1 | SU F1 INV5 | DcMs_Amp_01_F | A | 30.5.1112
SUINV5JB2 | 19 | DC current input 2 | SU F1 INV5 | DcMs_Amp_02_F | A | 30.5.1113
SUINV5JB2 | 20 | DC current input 3 | SU F1 INV5 | DcMs_Amp_03_F | A | 30.5.1114
SUINV5JB2 | 21 | DC current input 4 | SU F1 INV5 | DcMs_Amp_04_F | A | 30.5.1115
SUINV5JB2 | 22 | DC current input 5 | SU F1 INV5 | DcMs_Amp_05_F | A | 30.5.1116
SUINV5JB2 | 23 | DC current input 6 | SU F1 INV5 | DcMs_Amp_06_F | A | 30.5.1117
SUINV5JB2 | 24 | DC current input 7 | SU F1 INV5 | DcMs_Amp_07_F | A | 30.5.1118
SUINV5JB2 | 25 | DC current input 8 | SU F1 INV5 | DcMs_Amp_08_F | A | 30.5.1119
SUINV5JB2 | 26 | DC current input 9 | SU F1 INV5 | DcMs_Amp_09_F | A | 30.5.1120
SUINV5JB2 | 27 | DC current input 10 | SU F1 INV5 | DcMs_Amp_10_F | A | 30.5.1121
SUINV5JB2 | 28 | DC current input 11 | SU F1 INV5 | DcMs_Amp_11_F | A | 30.5.1122
SUINV5JB2 | 29 | DC current input 12 | SU F1 INV5 | DcMs_Amp_12_F | A | 30.5.1123
SUINV5JB2 | 30 | DC current input 13 | SU F1 INV5 | DcMs_Amp_13_F | A | 30.5.1124
SUINV5JB2 | 31 | DC current input 14 | SU F1 INV5 | DcMs_Amp_14_F | A | 30.5.1125
SUINV5JB2 | 32 | DC current input 15 | SU F1 INV5 | DcMs_Amp_15_F | A | 30.5.1126
SUINV5JB2 | 33 | DC current input 16 | SU F1 INV5 | DcMs_Amp_16_F | A | 30.5.1127
SUF1INV6 | 1 | DC voltage DC plus to DC minus | SU F1 INV6 | DcMs_Vol | V | 30.5.1128
SUF1INV6 | 2 | DC current inverter bridge 1 | SU F1 INV6 | DcMs_Amp_Stk1 | A | 30.5.1129
SUF1INV6 | 3 | DC current inverter bridge 2 | SU F1 INV6 | DcMs_Amp_Stk2 | A | 30.5.1130
SUF1INV6 | 4 | DC current inverter bridge 3 | SU F1 INV6 | DcMs_Amp_Stk3 | A | 30.5.1131
SUF1INV6 | 5 | DC current, total | SU F1 INV6 | DcMs_TotAmp | A | 30.5.1132
SUF1INV6 | 6 | DC power, total | SU F1 INV6 | DcMs_TotWatt | kW | 30.5.1133
SUF1INV6 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV6 | InvMs_DclVol_Stk1 | V | 30.5.1134
SUF1INV6 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV6 | InvMs_DclVol_Stk2 | V | 30.5.1135
SUF1INV6 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV6 | InvMs_DclVol_Stk3 | V | 30.5.1136
SUF1INV6 | 10 | AC current L1, total | SU F1 INV6 | InvMs_TotA_PhsA | A | 30.5.1137
SUF1INV6 | 11 | AC current L2, total | SU F1 INV6 | InvMs_TotA_PhsB | A | 30.5.1138
SUF1INV6 | 12 | AC current L3, total | SU F1 INV6 | InvMs_TotA_PhsC | A | 30.5.1139
SUF1INV6 | 13 | Power factor (cos phi) | SU F1 INV6 | InvMs_PF | "-" | 30.5.1140
SUF1INV6 | 14 | Apparent power, total | SU F1 INV6 | InvMs_TotVA | kVA | 30.5.1141
SUF1INV6 | 15 | Active power, total | SU F1 INV6 | InvMs_TotW | kW | 30.5.1142
SUF1INV6 | 16 | Reactive power, total | SU F1 INV6 | InvMs_TotVAr | kVAr | 30.5.1143
SUF1INV6 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV6 | GriMs_V_PhsAB | V | 30.5.1144
SUF1INV6 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV6 | GriMs_V_PhsBC | V | 30.5.1145
SUF1INV6 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV6 | GriMs_V_PhsCA | V | 30.5.1146
SUF1INV6 | 20 | Power frequency | SU F1 INV6 | GriMs_Hz | Hz | 30.5.1147
SUF1INV6 | 21 | Temperature in the AC range | SU F1 INV6 | TmpCab_Acc | °C | 30.5.1148
SUF1INV6 | 22 | Temperature in the DC range | SU F1 INV6 | TmpCab_Dcc | °C | 30.5.1149
SUF1INV6 | 23 | Temperature in the electronics area | SU F1 INV6 | TmpCab_Rio | °C | 30.5.1150
SUF1INV6 | 24 | Temperature in interior, maximum value | SU F1 INV6 | TmpCab_Max | °C | 30.5.1151
SUF1INV6 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV6 | TmpStk_IgbtMax | °C | 30.5.1152
SUF1INV6 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV6 | TmpStk_PcbMax | °C | 30.5.1153
SUF1INV6 | 27 | Outside temperature | SU F1 INV6 | TmpExl | ?C | 30.5.1154
SUF1INV6 | 28 | Temperature of the MV transformer | SU F1 INV6 | TmpTrf | °C | 30.5.1155
SUF1INV6 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV6 | DcSw1Stt | "-" | 30.5.1156
SUF1INV6 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV6 | DcSw2Stt | "-" | 30.5.1157
SUF1INV6 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV6 | DcSw3Stt | "-" | 30.5.1158
SUF1INV6 | 32 | Switching status of the AC circuit breaker | SU F1 INV6 | AcSwStt | "-" | 30.5.1159
SUF1INV6 | 33 | Switching state of the capacitor contactor | SU F1 INV6 | CapacSwStt | "-" | 30.5.1160
SUF1INV6 | 34 | Switching status of the pre-charging contactor | SU F1 INV6 | PrchrgSwStt | "-" | 30.5.1161
SUF1INV6 | 35 | Feed-in hours | SU F1 INV6 | Cnt_TotFeedTm | "-" | 30.5.1162
SUF1INV6 | 36 | Operating hours | SU F1 INV6 | Cnt_TotOpTm | "-" | 30.5.1163
SUF1INV6 | 37 | DC energy drawn, total | SU F1 INV6 | Cnt_TotWatthIn | MWh | 30.5.1164
SUF1INV6 | 38 | AC energy fed in, total | SU F1 INV6 | Cnt_TotWhOut | MWh | 30.5.1165
SUF1INV6 | 39 | DC energy drawn that day | SU F1 INV6 | Cnt_WatthIn | MWh | 30.5.1166
SUF1INV6 | 40 | AC energy fed in that day | SU F1 INV6 | Cnt_WhOut | MWh | 30.5.1167
SUF1INV6 | 41 | Operating hours of the interior fan 1 | SU F1 INV6 | Cnt_FanCab1Tm | "-" | 30.5.1168
SUF1INV6 | 42 | Operating hours of the interior fan 2 | SU F1 INV6 | Cnt_FanCab2Tm | "-" | 30.5.1169
SUF1INV6 | 43 | Operating hours of the inverter bridge fan | SU F1 INV6 | Cnt_FanStkTm | "-" | 30.5.1170
SUF1INV6 | 44 | Operating hours of the internal heating element | SU F1 INV6 | Cnt_HtCabTm | "-" | 30.5.1171
SUF1INV6 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV6 | Cnt_HtLoExlTmpTm | "-" | 30.5.1172
SUF1INV6 | 46 | Error location of the present error | SU F1 INV6 | ErrLcn | "-" | 30.5.1173
SUF1INV6 | 47 | Error status of the inverter | SU F1 INV6 | ErrStt | "-" | 30.5.1174
SUF1INV6 | 48 | Error number of the present error | SU F1 INV6 | ErrNo | "-" | 30.5.1175
SUF1INV6 | 49 | Operating state of the inverter | SU F1 INV6 | OpStt | "-" | 30.5.1176
SUF1INV6 | 50 | Switch status of the start-stop key switch | SU F1 INV6 | Rio_KeySw | "-" | 30.5.1177
SUF1INV6 | 51 | Waiting time for grid connection | SU F1 INV6 | WaitGriTm | s | 30.5.1178
SUF1INV6 | 52 | Inverter serial number | SU F1 INV6 | DevInf_SerNo | "-" | 30.5.1179
SUF1INV6 | 53 | Switching status of the GFDI | SU F1 INV6 | GfdiSwStt | "-" | 30.5.1180
SUF1INV6 | 54 | Active power, setpoint | SU F1 INV6 | WSpt | kW | 30.5.1181
SUF1INV6 | 55 | Maximum apparent power, setpoint | SU F1 INV6 | VAMaxSpt | kVA | 30.5.1182
SUF1INV6 | 56 | Reactive power, setpoint | SU F1 INV6 | VArSpt | kVAr | 30.5.1183
SUF1INV6 | 57 | Power factor cos (phi), setpoint | SU F1 INV6 | PFSpt | "-" | 30.5.1184
SUF1INV6 | 58 | Fast stop hermetic protection, pressure | SU F1 INV6 | TrfPro_Pres | "-" | 30.5.1185
SUF1INV6 | 59 | Fast stop hermetic protection, temperature | SU F1 INV6 | TrfPro_TmpTrp | "-" | 30.5.1186
SUF1INV6 | 60 | Hermetic protection, gas fill level | SU F1 INV6 | TrfPro_GasOilLev | "-" | 30.5.1187
SUF1INV6 | 61 | Hermetic pressure, temperature warning | SU F1 INV6 | TrfPro_TmpWrn | "-" | 30.5.1188
SUF1INV6 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV6 | TmpStk1_Igbt | °C | 30.5.1189
SUF1INV6 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV6 | TmpStk2_Igbt | °C | 30.5.1190
SUF1INV6 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV6 | TmpStk3_Igbt | °C | 30.5.1191
SUF1INV6 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV6 | TmpStk1_Pcb | ?C | 30.5.1192
SUF1INV6 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV6 | TmpStk2_Pcb | ?C | 30.5.1193
SUF1INV6 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV6 | TmpStk3_Pcb | ?C | 30.5.1194
SUF1INV6 | 68 | AC Energy Fed in the previous Day | SU F1 INV6 | Cnt_YstdWhOut | MWh | 30.5.1195
SUF1INV6 | 69 | CPU running time since system start | SU F1 INV6 | Cpu1UpTime | s | 30.5.1196
SUF1INV6 | 70 | Insulation resistance | SU F1 INV6 | PvGnd_RisIso | kOhm | 30.5.1197
SUF1INV6 | 71 | MV transformer pressure | SU F1 INV6 | PresTrf | "-" | 30.5.1198
SUF1INV6 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV6 | PresTrf_ErrStt | "-" | 30.5.1199
SUF1INV6 | 73 | DC voltage DC plus to DC minus | SU F1 INV6 | DcMs_Vol_F | V | 30.5.1200
SUF1INV6 | 74 | DC current inverter bridge 1 | SU F1 INV6 | DcMs_Amp_Stk1_F | A | 30.5.1201
SUF1INV6 | 75 | DC current inverter bridge 2 | SU F1 INV6 | DcMs_Amp_Stk2_F | A | 30.5.1202
SUF1INV6 | 76 | DC current inverter bridge 3 | SU F1 INV6 | DcMs_Amp_Stk3_F | A | 30.5.1203
SUF1INV6 | 77 | DC current, total | SU F1 INV6 | DcMs_TotAmp_F | A | 30.5.1204
SUF1INV6 | 78 | DC power, total | SU F1 INV6 | DcMs_TotWatt_F | kW | 30.5.1205
SUF1INV6 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV6 | InvMs_DclVol_Stk1_F | V | 30.5.1206
SUF1INV6 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV6 | InvMs_DclVol_Stk2_F | V | 30.5.1207
SUF1INV6 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV6 | InvMs_DclVol_Stk3_F | V | 30.5.1208
SUF1INV6 | 82 | AC current L1, total | SU F1 INV6 | InvMs_TotA_PhsA_F | A | 30.5.1209
SUF1INV6 | 83 | AC current L2, total | SU F1 INV6 | InvMs_TotA_PhsB_F | A | 30.5.1210
SUF1INV6 | 84 | AC current L3, total | SU F1 INV6 | InvMs_TotA_PhsC_F | A | 30.5.1211
SUF1INV6 | 85 | Power factor (cos phi) | SU F1 INV6 | InvMs_PF_F | "-" | 30.5.1212
SUF1INV6 | 86 | Active power, total | SU F1 INV6 | InvMs_TotW_F | kW | 30.5.1213
SUF1INV6 | 87 | Reactive power, total | SU F1 INV6 | InvMs_TotVAr_F | kVAr | 30.5.1214
SUF1INV6 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV6 | GriMs_V_PhsAB_F | V | 30.5.1215
SUF1INV6 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV6 | GriMs_V_PhsBC_F | V | 30.5.1216
SUF1INV6 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV6 | GriMs_V_PhsCA_F | V | 30.5.1217
SUF1INV6 | 91 | Power frequency | SU F1 INV6 | GriMs_Hz_F | Hz | 30.5.1218
SUF1INV6 | 92 | Temperature in the AC range | SU F1 INV6 | TmpCab_Acc_F | °C | 30.5.1219
SUF1INV6 | 93 | Temperature in the DC range | SU F1 INV6 | TmpCab_Dcc_F | °C | 30.5.1220
SUF1INV6 | 94 | Temperature in the electronics area | SU F1 INV6 | TmpCab_Rio_F | °C | 30.5.1221
SUF1INV6 | 95 | Temperature in interior, maximum value | SU F1 INV6 | TmpCab_Max_F | °C | 30.5.1222
SUF1INV6 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV6 | TmpStk_IgbtMax_F | °C | 30.5.1223
SUF1INV6 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV6 | TmpStk_PcbMax_F | °C | 30.5.1224
SUF1INV6 | 98 | Outside temperature | SU F1 INV6 | TmpExl_F | ?C | 30.5.1225
SUF1INV6 | 99 | Temperature of the MV transformer | SU F1 INV6 | TmpTrf_F | °C | 30.5.1226
SUF1INV6 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV6 | TmpStk1_Igbt_F | °C | 30.5.1227
SUF1INV6 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV6 | TmpStk2_Igbt_F | °C | 30.5.1228
SUF1INV6 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV6 | TmpStk3_Igbt_F | °C | 30.5.1229
SUF1INV6 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV6 | TmpStk1_Pcb_F | ?C | 30.5.1230
SUF1INV6 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV6 | TmpStk2_Pcb_F | ?C | 30.5.1231
SUF1INV6 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV6 | TmpStk3_Pcb_F | ?C | 30.5.1232
SUF1INV6 | 106 | MV transformer pressure | SU F1 INV6 | PresTrf_F | "-" | 30.5.1233
SUF1INV6 | 110 | Switching status of the DC load-break switch | SU F1 INV6 | DcSwStt | "-" | 30.5.1234
SUINV6JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV6 | Dat_UpdCnt_1 | "-" | 30.5.1235
SUINV6JB1 | 2 | DC current input 1 | SU F1 INV6 | DcMs_Amp_01 | A | 30.5.1236
SUINV6JB1 | 3 | DC current input 2 | SU F1 INV6 | DcMs_Amp_02 | A | 30.5.1237
SUINV6JB1 | 4 | DC current input 3 | SU F1 INV6 | DcMs_Amp_03 | A | 30.5.1238
SUINV6JB1 | 5 | DC current input 4 | SU F1 INV6 | DcMs_Amp_04 | A | 30.5.1239
SUINV6JB1 | 6 | DC current input 5 | SU F1 INV6 | DcMs_Amp_05 | A | 30.5.1240
SUINV6JB1 | 7 | DC current input 6 | SU F1 INV6 | DcMs_Amp_06 | A | 30.5.1241
SUINV6JB1 | 8 | DC current input 7 | SU F1 INV6 | DcMs_Amp_07 | A | 30.5.1242
SUINV6JB1 | 9 | DC current input 8 | SU F1 INV6 | DcMs_Amp_08 | A | 30.5.1243
SUINV6JB1 | 10 | DC current input 9 | SU F1 INV6 | DcMs_Amp_09 | A | 30.5.1244
SUINV6JB1 | 11 | DC current input 10 | SU F1 INV6 | DcMs_Amp_10 | A | 30.5.1245
SUINV6JB1 | 12 | DC current input 11 | SU F1 INV6 | DcMs_Amp_11 | A | 30.5.1246
SUINV6JB1 | 13 | DC current input 12 | SU F1 INV6 | DcMs_Amp_12 | A | 30.5.1247
SUINV6JB1 | 14 | DC current input 13 | SU F1 INV6 | DcMs_Amp_13 | A | 30.5.1248
SUINV6JB1 | 15 | DC current input 14 | SU F1 INV6 | DcMs_Amp_14 | A | 30.5.1249
SUINV6JB1 | 16 | DC current input 15 | SU F1 INV6 | DcMs_Amp_15 | A | 30.5.1250
SUINV6JB1 | 17 | DC current input 16 | SU F1 INV6 | DcMs_Amp_16 | A | 30.5.1251
SUINV6JB1 | 18 | DC current input 1 | SU F1 INV6 | DcMs_Amp_01_F | A | 30.5.1252
SUINV6JB1 | 19 | DC current input 2 | SU F1 INV6 | DcMs_Amp_02_F | A | 30.5.1253
SUINV6JB1 | 20 | DC current input 3 | SU F1 INV6 | DcMs_Amp_03_F | A | 30.5.1254
SUINV6JB1 | 21 | DC current input 4 | SU F1 INV6 | DcMs_Amp_04_F | A | 30.5.1255
SUINV6JB1 | 22 | DC current input 5 | SU F1 INV6 | DcMs_Amp_05_F | A | 30.5.1256
SUINV6JB1 | 23 | DC current input 6 | SU F1 INV6 | DcMs_Amp_06_F | A | 30.5.1257
SUINV6JB1 | 24 | DC current input 7 | SU F1 INV6 | DcMs_Amp_07_F | A | 30.5.1258
SUINV6JB1 | 25 | DC current input 8 | SU F1 INV6 | DcMs_Amp_08_F | A | 30.5.1259
SUINV6JB1 | 26 | DC current input 9 | SU F1 INV6 | DcMs_Amp_09_F | A | 30.5.1260
SUINV6JB1 | 27 | DC current input 10 | SU F1 INV6 | DcMs_Amp_10_F | A | 30.5.1261
SUINV6JB1 | 28 | DC current input 11 | SU F1 INV6 | DcMs_Amp_11_F | A | 30.5.1262
SUINV6JB1 | 29 | DC current input 12 | SU F1 INV6 | DcMs_Amp_12_F | A | 30.5.1263
SUINV6JB1 | 30 | DC current input 13 | SU F1 INV6 | DcMs_Amp_13_F | A | 30.5.1264
SUINV6JB1 | 31 | DC current input 14 | SU F1 INV6 | DcMs_Amp_14_F | A | 30.5.1265
SUINV6JB1 | 32 | DC current input 15 | SU F1 INV6 | DcMs_Amp_15_F | A | 30.5.1266
SUINV6JB1 | 33 | DC current input 16 | SU F1 INV6 | DcMs_Amp_16_F | A | 30.5.1267
SUINV6JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV6 | Dat_UpdCnt_1 | "-" | 30.5.1268
SUINV6JB2 | 2 | DC current input 1 | SU F1 INV6 | DcMs_Amp_01 | A | 30.5.1269
SUINV6JB2 | 3 | DC current input 2 | SU F1 INV6 | DcMs_Amp_02 | A | 30.5.1270
SUINV6JB2 | 4 | DC current input 3 | SU F1 INV6 | DcMs_Amp_03 | A | 30.5.1271
SUINV6JB2 | 5 | DC current input 4 | SU F1 INV6 | DcMs_Amp_04 | A | 30.5.1272
SUINV6JB2 | 6 | DC current input 5 | SU F1 INV6 | DcMs_Amp_05 | A | 30.5.1273
SUINV6JB2 | 7 | DC current input 6 | SU F1 INV6 | DcMs_Amp_06 | A | 30.5.1274
SUINV6JB2 | 8 | DC current input 7 | SU F1 INV6 | DcMs_Amp_07 | A | 30.5.1275
SUINV6JB2 | 9 | DC current input 8 | SU F1 INV6 | DcMs_Amp_08 | A | 30.5.1276
SUINV6JB2 | 10 | DC current input 9 | SU F1 INV6 | DcMs_Amp_09 | A | 30.5.1277
SUINV6JB2 | 11 | DC current input 10 | SU F1 INV6 | DcMs_Amp_10 | A | 30.5.1278
SUINV6JB2 | 12 | DC current input 11 | SU F1 INV6 | DcMs_Amp_11 | A | 30.5.1279
SUINV6JB2 | 13 | DC current input 12 | SU F1 INV6 | DcMs_Amp_12 | A | 30.5.1280
SUINV6JB2 | 14 | DC current input 13 | SU F1 INV6 | DcMs_Amp_13 | A | 30.5.1281
SUINV6JB2 | 15 | DC current input 14 | SU F1 INV6 | DcMs_Amp_14 | A | 30.5.1282
SUINV6JB2 | 16 | DC current input 15 | SU F1 INV6 | DcMs_Amp_15 | A | 30.5.1283
SUINV6JB2 | 17 | DC current input 16 | SU F1 INV6 | DcMs_Amp_16 | A | 30.5.1284
SUINV6JB2 | 18 | DC current input 1 | SU F1 INV6 | DcMs_Amp_01_F | A | 30.5.1285
SUINV6JB2 | 19 | DC current input 2 | SU F1 INV6 | DcMs_Amp_02_F | A | 30.5.1286
SUINV6JB2 | 20 | DC current input 3 | SU F1 INV6 | DcMs_Amp_03_F | A | 30.5.1287
SUINV6JB2 | 21 | DC current input 4 | SU F1 INV6 | DcMs_Amp_04_F | A | 30.5.1288
SUINV6JB2 | 22 | DC current input 5 | SU F1 INV6 | DcMs_Amp_05_F | A | 30.5.1289
SUINV6JB2 | 23 | DC current input 6 | SU F1 INV6 | DcMs_Amp_06_F | A | 30.5.1290
SUINV6JB2 | 24 | DC current input 7 | SU F1 INV6 | DcMs_Amp_07_F | A | 30.5.1291
SUINV6JB2 | 25 | DC current input 8 | SU F1 INV6 | DcMs_Amp_08_F | A | 30.5.1292
SUINV6JB2 | 26 | DC current input 9 | SU F1 INV6 | DcMs_Amp_09_F | A | 30.5.1293
SUINV6JB2 | 27 | DC current input 10 | SU F1 INV6 | DcMs_Amp_10_F | A | 30.5.1294
SUINV6JB2 | 28 | DC current input 11 | SU F1 INV6 | DcMs_Amp_11_F | A | 30.5.1295
SUINV6JB2 | 29 | DC current input 12 | SU F1 INV6 | DcMs_Amp_12_F | A | 30.5.1296
SUINV6JB2 | 30 | DC current input 13 | SU F1 INV6 | DcMs_Amp_13_F | A | 30.5.1297
SUINV6JB2 | 31 | DC current input 14 | SU F1 INV6 | DcMs_Amp_14_F | A | 30.5.1298
SUINV6JB2 | 32 | DC current input 15 | SU F1 INV6 | DcMs_Amp_15_F | A | 30.5.1299
SUINV6JB2 | 33 | DC current input 16 | SU F1 INV6 | DcMs_Amp_16_F | A | 30.5.1300
SUF1INV7 | 1 | DC voltage DC plus to DC minus | SU F1 INV7 | DcMs_Vol | V | 30.5.1301
SUF1INV7 | 2 | DC current inverter bridge 1 | SU F1 INV7 | DcMs_Amp_Stk1 | A | 30.5.1302
SUF1INV7 | 3 | DC current inverter bridge 2 | SU F1 INV7 | DcMs_Amp_Stk2 | A | 30.5.1303
SUF1INV7 | 4 | DC current inverter bridge 3 | SU F1 INV7 | DcMs_Amp_Stk3 | A | 30.5.1304
SUF1INV7 | 5 | DC current, total | SU F1 INV7 | DcMs_TotAmp | A | 30.5.1305
SUF1INV7 | 6 | DC power, total | SU F1 INV7 | DcMs_TotWatt | kW | 30.5.1306
SUF1INV7 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV7 | InvMs_DclVol_Stk1 | V | 30.5.1307
SUF1INV7 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV7 | InvMs_DclVol_Stk2 | V | 30.5.1308
SUF1INV7 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV7 | InvMs_DclVol_Stk3 | V | 30.5.1309
SUF1INV7 | 10 | AC current L1, total | SU F1 INV7 | InvMs_TotA_PhsA | A | 30.5.1310
SUF1INV7 | 11 | AC current L2, total | SU F1 INV7 | InvMs_TotA_PhsB | A | 30.5.1311
SUF1INV7 | 12 | AC current L3, total | SU F1 INV7 | InvMs_TotA_PhsC | A | 30.5.1312
SUF1INV7 | 13 | Power factor (cos phi) | SU F1 INV7 | InvMs_PF | "-" | 30.5.1313
SUF1INV7 | 14 | Apparent power, total | SU F1 INV7 | InvMs_TotVA | kVA | 30.5.1314
SUF1INV7 | 15 | Active power, total | SU F1 INV7 | InvMs_TotW | kW | 30.5.1315
SUF1INV7 | 16 | Reactive power, total | SU F1 INV7 | InvMs_TotVAr | kVAr | 30.5.1316
SUF1INV7 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV7 | GriMs_V_PhsAB | V | 30.5.1317
SUF1INV7 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV7 | GriMs_V_PhsBC | V | 30.5.1318
SUF1INV7 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV7 | GriMs_V_PhsCA | V | 30.5.1319
SUF1INV7 | 20 | Power frequency | SU F1 INV7 | GriMs_Hz | Hz | 30.5.1320
SUF1INV7 | 21 | Temperature in the AC range | SU F1 INV7 | TmpCab_Acc | °C | 30.5.1321
SUF1INV7 | 22 | Temperature in the DC range | SU F1 INV7 | TmpCab_Dcc | °C | 30.5.1322
SUF1INV7 | 23 | Temperature in the electronics area | SU F1 INV7 | TmpCab_Rio | °C | 30.5.1323
SUF1INV7 | 24 | Temperature in interior, maximum value | SU F1 INV7 | TmpCab_Max | °C | 30.5.1324
SUF1INV7 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV7 | TmpStk_IgbtMax | °C | 30.5.1325
SUF1INV7 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV7 | TmpStk_PcbMax | °C | 30.5.1326
SUF1INV7 | 27 | Outside temperature | SU F1 INV7 | TmpExl | ?C | 30.5.1327
SUF1INV7 | 28 | Temperature of the MV transformer | SU F1 INV7 | TmpTrf | °C | 30.5.1328
SUF1INV7 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV7 | DcSw1Stt | "-" | 30.5.1329
SUF1INV7 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV7 | DcSw2Stt | "-" | 30.5.1330
SUF1INV7 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV7 | DcSw3Stt | "-" | 30.5.1331
SUF1INV7 | 32 | Switching status of the AC circuit breaker | SU F1 INV7 | AcSwStt | "-" | 30.5.1332
SUF1INV7 | 33 | Switching state of the capacitor contactor | SU F1 INV7 | CapacSwStt | "-" | 30.5.1333
SUF1INV7 | 34 | Switching status of the pre-charging contactor | SU F1 INV7 | PrchrgSwStt | "-" | 30.5.1334
SUF1INV7 | 35 | Feed-in hours | SU F1 INV7 | Cnt_TotFeedTm | "-" | 30.5.1335
SUF1INV7 | 36 | Operating hours | SU F1 INV7 | Cnt_TotOpTm | "-" | 30.5.1336
SUF1INV7 | 37 | DC energy drawn, total | SU F1 INV7 | Cnt_TotWatthIn | MWh | 30.5.1337
SUF1INV7 | 38 | AC energy fed in, total | SU F1 INV7 | Cnt_TotWhOut | MWh | 30.5.1338
SUF1INV7 | 39 | DC energy drawn that day | SU F1 INV7 | Cnt_WatthIn | MWh | 30.5.1339
SUF1INV7 | 40 | AC energy fed in that day | SU F1 INV7 | Cnt_WhOut | MWh | 30.5.1340
SUF1INV7 | 41 | Operating hours of the interior fan 1 | SU F1 INV7 | Cnt_FanCab1Tm | "-" | 30.5.1341
SUF1INV7 | 42 | Operating hours of the interior fan 2 | SU F1 INV7 | Cnt_FanCab2Tm | "-" | 30.5.1342
SUF1INV7 | 43 | Operating hours of the inverter bridge fan | SU F1 INV7 | Cnt_FanStkTm | "-" | 30.5.1343
SUF1INV7 | 44 | Operating hours of the internal heating element | SU F1 INV7 | Cnt_HtCabTm | "-" | 30.5.1344
SUF1INV7 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV7 | Cnt_HtLoExlTmpTm | "-" | 30.5.1345
SUF1INV7 | 46 | Error location of the present error | SU F1 INV7 | ErrLcn | "-" | 30.5.1346
SUF1INV7 | 47 | Error status of the inverter | SU F1 INV7 | ErrStt | "-" | 30.5.1347
SUF1INV7 | 48 | Error number of the present error | SU F1 INV7 | ErrNo | "-" | 30.5.1348
SUF1INV7 | 49 | Operating state of the inverter | SU F1 INV7 | OpStt | "-" | 30.5.1349
SUF1INV7 | 50 | Switch status of the start-stop key switch | SU F1 INV7 | Rio_KeySw | "-" | 30.5.1350
SUF1INV7 | 51 | Waiting time for grid connection | SU F1 INV7 | WaitGriTm | s | 30.5.1351
SUF1INV7 | 52 | Inverter serial number | SU F1 INV7 | DevInf_SerNo | "-" | 30.5.1352
SUF1INV7 | 53 | Switching status of the GFDI | SU F1 INV7 | GfdiSwStt | "-" | 30.5.1353
SUF1INV7 | 54 | Active power, setpoint | SU F1 INV7 | WSpt | kW | 30.5.1354
SUF1INV7 | 55 | Maximum apparent power, setpoint | SU F1 INV7 | VAMaxSpt | kVA | 30.5.1355
SUF1INV7 | 56 | Reactive power, setpoint | SU F1 INV7 | VArSpt | kVAr | 30.5.1356
SUF1INV7 | 57 | Power factor cos (phi), setpoint | SU F1 INV7 | PFSpt | "-" | 30.5.1357
SUF1INV7 | 58 | Fast stop hermetic protection, pressure | SU F1 INV7 | TrfPro_Pres | "-" | 30.5.1358
SUF1INV7 | 59 | Fast stop hermetic protection, temperature | SU F1 INV7 | TrfPro_TmpTrp | "-" | 30.5.1359
SUF1INV7 | 60 | Hermetic protection, gas fill level | SU F1 INV7 | TrfPro_GasOilLev | "-" | 30.5.1360
SUF1INV7 | 61 | Hermetic pressure, temperature warning | SU F1 INV7 | TrfPro_TmpWrn | "-" | 30.5.1361
SUF1INV7 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV7 | TmpStk1_Igbt | °C | 30.5.1362
SUF1INV7 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV7 | TmpStk2_Igbt | °C | 30.5.1363
SUF1INV7 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV7 | TmpStk3_Igbt | °C | 30.5.1364
SUF1INV7 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV7 | TmpStk1_Pcb | ?C | 30.5.1365
SUF1INV7 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV7 | TmpStk2_Pcb | ?C | 30.5.1366
SUF1INV7 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV7 | TmpStk3_Pcb | ?C | 30.5.1367
SUF1INV7 | 68 | AC Energy Fed in the previous Day | SU F1 INV7 | Cnt_YstdWhOut | MWh | 30.5.1368
SUF1INV7 | 69 | CPU running time since system start | SU F1 INV7 | Cpu1UpTime | s | 30.5.1369
SUF1INV7 | 70 | Insulation resistance | SU F1 INV7 | PvGnd_RisIso | kOhm | 30.5.1370
SUF1INV7 | 71 | MV transformer pressure | SU F1 INV7 | PresTrf | "-" | 30.5.1371
SUF1INV7 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV7 | PresTrf_ErrStt | "-" | 30.5.1372
SUF1INV7 | 73 | DC voltage DC plus to DC minus | SU F1 INV7 | DcMs_Vol_F | V | 30.5.1373
SUF1INV7 | 74 | DC current inverter bridge 1 | SU F1 INV7 | DcMs_Amp_Stk1_F | A | 30.5.1374
SUF1INV7 | 75 | DC current inverter bridge 2 | SU F1 INV7 | DcMs_Amp_Stk2_F | A | 30.5.1375
SUF1INV7 | 76 | DC current inverter bridge 3 | SU F1 INV7 | DcMs_Amp_Stk3_F | A | 30.5.1376
SUF1INV7 | 77 | DC current, total | SU F1 INV7 | DcMs_TotAmp_F | A | 30.5.1377
SUF1INV7 | 78 | DC power, total | SU F1 INV7 | DcMs_TotWatt_F | kW | 30.5.1378
SUF1INV7 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV7 | InvMs_DclVol_Stk1_F | V | 30.5.1379
SUF1INV7 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV7 | InvMs_DclVol_Stk2_F | V | 30.5.1380
SUF1INV7 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV7 | InvMs_DclVol_Stk3_F | V | 30.5.1381
SUF1INV7 | 82 | AC current L1, total | SU F1 INV7 | InvMs_TotA_PhsA_F | A | 30.5.1382
SUF1INV7 | 83 | AC current L2, total | SU F1 INV7 | InvMs_TotA_PhsB_F | A | 30.5.1383
SUF1INV7 | 84 | AC current L3, total | SU F1 INV7 | InvMs_TotA_PhsC_F | A | 30.5.1384
SUF1INV7 | 85 | Power factor (cos phi) | SU F1 INV7 | InvMs_PF_F | "-" | 30.5.1385
SUF1INV7 | 86 | Active power, total | SU F1 INV7 | InvMs_TotW_F | kW | 30.5.1386
SUF1INV7 | 87 | Reactive power, total | SU F1 INV7 | InvMs_TotVAr_F | kVAr | 30.5.1387
SUF1INV7 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV7 | GriMs_V_PhsAB_F | V | 30.5.1388
SUF1INV7 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV7 | GriMs_V_PhsBC_F | V | 30.5.1389
SUF1INV7 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV7 | GriMs_V_PhsCA_F | V | 30.5.1390
SUF1INV7 | 91 | Power frequency | SU F1 INV7 | GriMs_Hz_F | Hz | 30.5.1391
SUF1INV7 | 92 | Temperature in the AC range | SU F1 INV7 | TmpCab_Acc_F | °C | 30.5.1392
SUF1INV7 | 93 | Temperature in the DC range | SU F1 INV7 | TmpCab_Dcc_F | °C | 30.5.1393
SUF1INV7 | 94 | Temperature in the electronics area | SU F1 INV7 | TmpCab_Rio_F | °C | 30.5.1394
SUF1INV7 | 95 | Temperature in interior, maximum value | SU F1 INV7 | TmpCab_Max_F | °C | 30.5.1395
SUF1INV7 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV7 | TmpStk_IgbtMax_F | °C | 30.5.1396
SUF1INV7 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV7 | TmpStk_PcbMax_F | °C | 30.5.1397
SUF1INV7 | 98 | Outside temperature | SU F1 INV7 | TmpExl_F | ?C | 30.5.1398
SUF1INV7 | 99 | Temperature of the MV transformer | SU F1 INV7 | TmpTrf_F | °C | 30.5.1399
SUF1INV7 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV7 | TmpStk1_Igbt_F | °C | 30.5.1400
SUF1INV7 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV7 | TmpStk2_Igbt_F | °C | 30.5.1401
SUF1INV7 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV7 | TmpStk3_Igbt_F | °C | 30.5.1402
SUF1INV7 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV7 | TmpStk1_Pcb_F | ?C | 30.5.1403
SUF1INV7 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV7 | TmpStk2_Pcb_F | ?C | 30.5.1404
SUF1INV7 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV7 | TmpStk3_Pcb_F | ?C | 30.5.1405
SUF1INV7 | 106 | MV transformer pressure | SU F1 INV7 | PresTrf_F | "-" | 30.5.1406
SUF1INV7 | 110 | Switching status of the DC load-break switch | SU F1 INV7 | DcSwStt | "-" | 30.5.1407
SUINV7JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV7 | Dat_UpdCnt_1 | "-" | 30.5.1408
SUINV7JB1 | 2 | DC current input 1 | SU F1 INV7 | DcMs_Amp_01 | A | 30.5.1409
SUINV7JB1 | 3 | DC current input 2 | SU F1 INV7 | DcMs_Amp_02 | A | 30.5.1410
SUINV7JB1 | 4 | DC current input 3 | SU F1 INV7 | DcMs_Amp_03 | A | 30.5.1411
SUINV7JB1 | 5 | DC current input 4 | SU F1 INV7 | DcMs_Amp_04 | A | 30.5.1412
SUINV7JB1 | 6 | DC current input 5 | SU F1 INV7 | DcMs_Amp_05 | A | 30.5.1413
SUINV7JB1 | 7 | DC current input 6 | SU F1 INV7 | DcMs_Amp_06 | A | 30.5.1414
SUINV7JB1 | 8 | DC current input 7 | SU F1 INV7 | DcMs_Amp_07 | A | 30.5.1415
SUINV7JB1 | 9 | DC current input 8 | SU F1 INV7 | DcMs_Amp_08 | A | 30.5.1416
SUINV7JB1 | 10 | DC current input 9 | SU F1 INV7 | DcMs_Amp_09 | A | 30.5.1417
SUINV7JB1 | 11 | DC current input 10 | SU F1 INV7 | DcMs_Amp_10 | A | 30.5.1418
SUINV7JB1 | 12 | DC current input 11 | SU F1 INV7 | DcMs_Amp_11 | A | 30.5.1419
SUINV7JB1 | 13 | DC current input 12 | SU F1 INV7 | DcMs_Amp_12 | A | 30.5.1420
SUINV7JB1 | 14 | DC current input 13 | SU F1 INV7 | DcMs_Amp_13 | A | 30.5.1421
SUINV7JB1 | 15 | DC current input 14 | SU F1 INV7 | DcMs_Amp_14 | A | 30.5.1422
SUINV7JB1 | 16 | DC current input 15 | SU F1 INV7 | DcMs_Amp_15 | A | 30.5.1423
SUINV7JB1 | 17 | DC current input 16 | SU F1 INV7 | DcMs_Amp_16 | A | 30.5.1424
SUINV7JB1 | 18 | DC current input 1 | SU F1 INV7 | DcMs_Amp_01_F | A | 30.5.1425
SUINV7JB1 | 19 | DC current input 2 | SU F1 INV7 | DcMs_Amp_02_F | A | 30.5.1426
SUINV7JB1 | 20 | DC current input 3 | SU F1 INV7 | DcMs_Amp_03_F | A | 30.5.1427
SUINV7JB1 | 21 | DC current input 4 | SU F1 INV7 | DcMs_Amp_04_F | A | 30.5.1428
SUINV7JB1 | 22 | DC current input 5 | SU F1 INV7 | DcMs_Amp_05_F | A | 30.5.1429
SUINV7JB1 | 23 | DC current input 6 | SU F1 INV7 | DcMs_Amp_06_F | A | 30.5.1430
SUINV7JB1 | 24 | DC current input 7 | SU F1 INV7 | DcMs_Amp_07_F | A | 30.5.1431
SUINV7JB1 | 25 | DC current input 8 | SU F1 INV7 | DcMs_Amp_08_F | A | 30.5.1432
SUINV7JB1 | 26 | DC current input 9 | SU F1 INV7 | DcMs_Amp_09_F | A | 30.5.1433
SUINV7JB1 | 27 | DC current input 10 | SU F1 INV7 | DcMs_Amp_10_F | A | 30.5.1434
SUINV7JB1 | 28 | DC current input 11 | SU F1 INV7 | DcMs_Amp_11_F | A | 30.5.1435
SUINV7JB1 | 29 | DC current input 12 | SU F1 INV7 | DcMs_Amp_12_F | A | 30.5.1436
SUINV7JB1 | 30 | DC current input 13 | SU F1 INV7 | DcMs_Amp_13_F | A | 30.5.1437
SUINV7JB1 | 31 | DC current input 14 | SU F1 INV7 | DcMs_Amp_14_F | A | 30.5.1438
SUINV7JB1 | 32 | DC current input 15 | SU F1 INV7 | DcMs_Amp_15_F | A | 30.5.1439
SUINV7JB1 | 33 | DC current input 16 | SU F1 INV7 | DcMs_Amp_16_F | A | 30.5.1440
SUINV7JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV7 | Dat_UpdCnt_1 | "-" | 30.5.1441
SUINV7JB2 | 2 | DC current input 1 | SU F1 INV7 | DcMs_Amp_01 | A | 30.5.1442
SUINV7JB2 | 3 | DC current input 2 | SU F1 INV7 | DcMs_Amp_02 | A | 30.5.1443
SUINV7JB2 | 4 | DC current input 3 | SU F1 INV7 | DcMs_Amp_03 | A | 30.5.1444
SUINV7JB2 | 5 | DC current input 4 | SU F1 INV7 | DcMs_Amp_04 | A | 30.5.1445
SUINV7JB2 | 6 | DC current input 5 | SU F1 INV7 | DcMs_Amp_05 | A | 30.5.1446
SUINV7JB2 | 7 | DC current input 6 | SU F1 INV7 | DcMs_Amp_06 | A | 30.5.1447
SUINV7JB2 | 8 | DC current input 7 | SU F1 INV7 | DcMs_Amp_07 | A | 30.5.1448
SUINV7JB2 | 9 | DC current input 8 | SU F1 INV7 | DcMs_Amp_08 | A | 30.5.1449
SUINV7JB2 | 10 | DC current input 9 | SU F1 INV7 | DcMs_Amp_09 | A | 30.5.1450
SUINV7JB2 | 11 | DC current input 10 | SU F1 INV7 | DcMs_Amp_10 | A | 30.5.1451
SUINV7JB2 | 12 | DC current input 11 | SU F1 INV7 | DcMs_Amp_11 | A | 30.5.1452
SUINV7JB2 | 13 | DC current input 12 | SU F1 INV7 | DcMs_Amp_12 | A | 30.5.1453
SUINV7JB2 | 14 | DC current input 13 | SU F1 INV7 | DcMs_Amp_13 | A | 30.5.1454
SUINV7JB2 | 15 | DC current input 14 | SU F1 INV7 | DcMs_Amp_14 | A | 30.5.1455
SUINV7JB2 | 16 | DC current input 15 | SU F1 INV7 | DcMs_Amp_15 | A | 30.5.1456
SUINV7JB2 | 17 | DC current input 16 | SU F1 INV7 | DcMs_Amp_16 | A | 30.5.1457
SUINV7JB2 | 18 | DC current input 1 | SU F1 INV7 | DcMs_Amp_01_F | A | 30.5.1458
SUINV7JB2 | 19 | DC current input 2 | SU F1 INV7 | DcMs_Amp_02_F | A | 30.5.1459
SUINV7JB2 | 20 | DC current input 3 | SU F1 INV7 | DcMs_Amp_03_F | A | 30.5.1460
SUINV7JB2 | 21 | DC current input 4 | SU F1 INV7 | DcMs_Amp_04_F | A | 30.5.1461
SUINV7JB2 | 22 | DC current input 5 | SU F1 INV7 | DcMs_Amp_05_F | A | 30.5.1462
SUINV7JB2 | 23 | DC current input 6 | SU F1 INV7 | DcMs_Amp_06_F | A | 30.5.1463
SUINV7JB2 | 24 | DC current input 7 | SU F1 INV7 | DcMs_Amp_07_F | A | 30.5.1464
SUINV7JB2 | 25 | DC current input 8 | SU F1 INV7 | DcMs_Amp_08_F | A | 30.5.1465
SUINV7JB2 | 26 | DC current input 9 | SU F1 INV7 | DcMs_Amp_09_F | A | 30.5.1466
SUINV7JB2 | 27 | DC current input 10 | SU F1 INV7 | DcMs_Amp_10_F | A | 30.5.1467
SUINV7JB2 | 28 | DC current input 11 | SU F1 INV7 | DcMs_Amp_11_F | A | 30.5.1468
SUINV7JB2 | 29 | DC current input 12 | SU F1 INV7 | DcMs_Amp_12_F | A | 30.5.1469
SUINV7JB2 | 30 | DC current input 13 | SU F1 INV7 | DcMs_Amp_13_F | A | 30.5.1470
SUINV7JB2 | 31 | DC current input 14 | SU F1 INV7 | DcMs_Amp_14_F | A | 30.5.1471
SUINV7JB2 | 32 | DC current input 15 | SU F1 INV7 | DcMs_Amp_15_F | A | 30.5.1472
SUINV7JB2 | 33 | DC current input 16 | SU F1 INV7 | DcMs_Amp_16_F | A | 30.5.1473
SUF1INV9 | 1 | DC voltage DC plus to DC minus | SU F1 INV9 | DcMs_Vol | V | 30.5.1474
SUF1INV9 | 2 | DC current inverter bridge 1 | SU F1 INV9 | DcMs_Amp_Stk1 | A | 30.5.1475
SUF1INV9 | 3 | DC current inverter bridge 2 | SU F1 INV9 | DcMs_Amp_Stk2 | A | 30.5.1476
SUF1INV9 | 4 | DC current inverter bridge 3 | SU F1 INV9 | DcMs_Amp_Stk3 | A | 30.5.1477
SUF1INV9 | 5 | DC current, total | SU F1 INV9 | DcMs_TotAmp | A | 30.5.1478
SUF1INV9 | 6 | DC power, total | SU F1 INV9 | DcMs_TotWatt | kW | 30.5.1479
SUF1INV9 | 7 | DC voltage of the inverter bridge 1 | SU F1 INV9 | InvMs_DclVol_Stk1 | V | 30.5.1480
SUF1INV9 | 8 | DC voltage of the inverter bridge 2 | SU F1 INV9 | InvMs_DclVol_Stk2 | V | 30.5.1481
SUF1INV9 | 9 | DC voltage of the inverter bridge 3 | SU F1 INV9 | InvMs_DclVol_Stk3 | V | 30.5.1482
SUF1INV9 | 10 | AC current L1, total | SU F1 INV9 | InvMs_TotA_PhsA | A | 30.5.1483
SUF1INV9 | 11 | AC current L2, total | SU F1 INV9 | InvMs_TotA_PhsB | A | 30.5.1484
SUF1INV9 | 12 | AC current L3, total | SU F1 INV9 | InvMs_TotA_PhsC | A | 30.5.1485
SUF1INV9 | 13 | Power factor (cos phi) | SU F1 INV9 | InvMs_PF | "-" | 30.5.1486
SUF1INV9 | 14 | Apparent power, total | SU F1 INV9 | InvMs_TotVA | kVA | 30.5.1487
SUF1INV9 | 15 | Active power, total | SU F1 INV9 | InvMs_TotW | kW | 30.5.1488
SUF1INV9 | 16 | Reactive power, total | SU F1 INV9 | InvMs_TotVAr | kVAr | 30.5.1489
SUF1INV9 | 17 | Line-to-line voltage L1-L2, utility grid | SU F1 INV9 | GriMs_V_PhsAB | V | 30.5.1490
SUF1INV9 | 18 | Line-to-line voltage L2-L3, utility grid | SU F1 INV9 | GriMs_V_PhsBC | V | 30.5.1491
SUF1INV9 | 19 | Line-to-line voltage L3-L1, utility grid | SU F1 INV9 | GriMs_V_PhsCA | V | 30.5.1492
SUF1INV9 | 20 | Power frequency | SU F1 INV9 | GriMs_Hz | Hz | 30.5.1493
SUF1INV9 | 21 | Temperature in the AC range | SU F1 INV9 | TmpCab_Acc | °C | 30.5.1494
SUF1INV9 | 22 | Temperature in the DC range | SU F1 INV9 | TmpCab_Dcc | °C | 30.5.1495
SUF1INV9 | 23 | Temperature in the electronics area | SU F1 INV9 | TmpCab_Rio | °C | 30.5.1496
SUF1INV9 | 24 | Temperature in interior, maximum value | SU F1 INV9 | TmpCab_Max | °C | 30.5.1497
SUF1INV9 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV9 | TmpStk_IgbtMax | °C | 30.5.1498
SUF1INV9 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV9 | TmpStk_PcbMax | °C | 30.5.1499
SUF1INV9 | 27 | Outside temperature | SU F1 INV9 | TmpExl | ?C | 30.5.1500
SUF1INV9 | 28 | Temperature of the MV transformer | SU F1 INV9 | TmpTrf | °C | 30.5.1501
SUF1INV9 | 29 | Switching status of the DC load-break switch 1 | SU F1 INV9 | DcSw1Stt | "-" | 30.5.1502
SUF1INV9 | 30 | Switching status of the DC load-break switch 2 | SU F1 INV9 | DcSw2Stt | "-" | 30.5.1503
SUF1INV9 | 31 | Switching status of the DC load-break switch 3 | SU F1 INV9 | DcSw3Stt | "-" | 30.5.1504
SUF1INV9 | 32 | Switching status of the AC circuit breaker | SU F1 INV9 | AcSwStt | "-" | 30.5.1505
SUF1INV9 | 33 | Switching state of the capacitor contactor | SU F1 INV9 | CapacSwStt | "-" | 30.5.1506
SUF1INV9 | 34 | Switching status of the pre-charging contactor | SU F1 INV9 | PrchrgSwStt | "-" | 30.5.1507
SUF1INV9 | 35 | Feed-in hours | SU F1 INV9 | Cnt_TotFeedTm | "-" | 30.5.1508
SUF1INV9 | 36 | Operating hours | SU F1 INV9 | Cnt_TotOpTm | "-" | 30.5.1509
SUF1INV9 | 37 | DC energy drawn, total | SU F1 INV9 | Cnt_TotWatthIn | MWh | 30.5.1510
SUF1INV9 | 38 | AC energy fed in, total | SU F1 INV9 | Cnt_TotWhOut | MWh | 30.5.1511
SUF1INV9 | 39 | DC energy drawn that day | SU F1 INV9 | Cnt_WatthIn | MWh | 30.5.1512
SUF1INV9 | 40 | AC energy fed in that day | SU F1 INV9 | Cnt_WhOut | MWh | 30.5.1513
SUF1INV9 | 41 | Operating hours of the interior fan 1 | SU F1 INV9 | Cnt_FanCab1Tm | "-" | 30.5.1514
SUF1INV9 | 42 | Operating hours of the interior fan 2 | SU F1 INV9 | Cnt_FanCab2Tm | "-" | 30.5.1515
SUF1INV9 | 43 | Operating hours of the inverter bridge fan | SU F1 INV9 | Cnt_FanStkTm | "-" | 30.5.1516
SUF1INV9 | 44 | Operating hours of the internal heating element | SU F1 INV9 | Cnt_HtCabTm | "-" | 30.5.1517
SUF1INV9 | 45 | Operating hours of the -40?C internal heating element | SU F1 INV9 | Cnt_HtLoExlTmpTm | "-" | 30.5.1518
SUF1INV9 | 46 | Error location of the present error | SU F1 INV9 | ErrLcn | "-" | 30.5.1519
SUF1INV9 | 47 | Error status of the inverter | SU F1 INV9 | ErrStt | "-" | 30.5.1520
SUF1INV9 | 48 | Error number of the present error | SU F1 INV9 | ErrNo | "-" | 30.5.1521
SUF1INV9 | 49 | Operating state of the inverter | SU F1 INV9 | OpStt | "-" | 30.5.1522
SUF1INV9 | 50 | Switch status of the start-stop key switch | SU F1 INV9 | Rio_KeySw | "-" | 30.5.1523
SUF1INV9 | 51 | Waiting time for grid connection | SU F1 INV9 | WaitGriTm | s | 30.5.1524
SUF1INV9 | 52 | Inverter serial number | SU F1 INV9 | DevInf_SerNo | "-" | 30.5.1525
SUF1INV9 | 53 | Switching status of the GFDI | SU F1 INV9 | GfdiSwStt | "-" | 30.5.1526
SUF1INV9 | 54 | Active power, setpoint | SU F1 INV9 | WSpt | kW | 30.5.1527
SUF1INV9 | 55 | Maximum apparent power, setpoint | SU F1 INV9 | VAMaxSpt | kVA | 30.5.1528
SUF1INV9 | 56 | Reactive power, setpoint | SU F1 INV9 | VArSpt | kVAr | 30.5.1529
SUF1INV9 | 57 | Power factor cos (phi), setpoint | SU F1 INV9 | PFSpt | "-" | 30.5.1530
SUF1INV9 | 58 | Fast stop hermetic protection, pressure | SU F1 INV9 | TrfPro_Pres | "-" | 30.5.1531
SUF1INV9 | 59 | Fast stop hermetic protection, temperature | SU F1 INV9 | TrfPro_TmpTrp | "-" | 30.5.1532
SUF1INV9 | 60 | Hermetic protection, gas fill level | SU F1 INV9 | TrfPro_GasOilLev | "-" | 30.5.1533
SUF1INV9 | 61 | Hermetic pressure, temperature warning | SU F1 INV9 | TrfPro_TmpWrn | "-" | 30.5.1534
SUF1INV9 | 62 | Temperature of inverter bridge 1 (switch) | SU F1 INV9 | TmpStk1_Igbt | °C | 30.5.1535
SUF1INV9 | 63 | Temperature of inverter bridge 2 (switch) | SU F1 INV9 | TmpStk2_Igbt | °C | 30.5.1536
SUF1INV9 | 64 | Temperature of inverter bridge 3 (switch) | SU F1 INV9 | TmpStk3_Igbt | °C | 30.5.1537
SUF1INV9 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV9 | TmpStk1_Pcb | ?C | 30.5.1538
SUF1INV9 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV9 | TmpStk2_Pcb | ?C | 30.5.1539
SUF1INV9 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV9 | TmpStk3_Pcb | ?C | 30.5.1540
SUF1INV9 | 68 | AC Energy Fed in the previous Day | SU F1 INV9 | Cnt_YstdWhOut | MWh | 30.5.1541
SUF1INV9 | 69 | CPU running time since system start | SU F1 INV9 | Cpu1UpTime | s | 30.5.1542
SUF1INV9 | 70 | Insulation resistance | SU F1 INV9 | PvGnd_RisIso | kOhm | 30.5.1543
SUF1INV9 | 71 | MV transformer pressure | SU F1 INV9 | PresTrf | "-" | 30.5.1544
SUF1INV9 | 72 | Error status of MV transformer pressure monitoring | SU F1 INV9 | PresTrf_ErrStt | "-" | 30.5.1545
SUF1INV9 | 73 | DC voltage DC plus to DC minus | SU F1 INV9 | DcMs_Vol_F | V | 30.5.1546
SUF1INV9 | 74 | DC current inverter bridge 1 | SU F1 INV9 | DcMs_Amp_Stk1_F | A | 30.5.1547
SUF1INV9 | 75 | DC current inverter bridge 2 | SU F1 INV9 | DcMs_Amp_Stk2_F | A | 30.5.1548
SUF1INV9 | 76 | DC current inverter bridge 3 | SU F1 INV9 | DcMs_Amp_Stk3_F | A | 30.5.1549
SUF1INV9 | 77 | DC current, total | SU F1 INV9 | DcMs_TotAmp_F | A | 30.5.1550
SUF1INV9 | 78 | DC power, total | SU F1 INV9 | DcMs_TotWatt_F | kW | 30.5.1551
SUF1INV9 | 79 | DC voltage of the inverter bridge 1 | SU F1 INV9 | InvMs_DclVol_Stk1_F | V | 30.5.1552
SUF1INV9 | 80 | DC voltage of the inverter bridge 2 | SU F1 INV9 | InvMs_DclVol_Stk2_F | V | 30.5.1553
SUF1INV9 | 81 | DC voltage of the inverter bridge 3 | SU F1 INV9 | InvMs_DclVol_Stk3_F | V | 30.5.1554
SUF1INV9 | 82 | AC current L1, total | SU F1 INV9 | InvMs_TotA_PhsA_F | A | 30.5.1555
SUF1INV9 | 83 | AC current L2, total | SU F1 INV9 | InvMs_TotA_PhsB_F | A | 30.5.1556
SUF1INV9 | 84 | AC current L3, total | SU F1 INV9 | InvMs_TotA_PhsC_F | A | 30.5.1557
SUF1INV9 | 85 | Power factor (cos phi) | SU F1 INV9 | InvMs_PF_F | "-" | 30.5.1558
SUF1INV9 | 86 | Active power, total | SU F1 INV9 | InvMs_TotW_F | kW | 30.5.1559
SUF1INV9 | 87 | Reactive power, total | SU F1 INV9 | InvMs_TotVAr_F | kVAr | 30.5.1560
SUF1INV9 | 88 | Line-to-line voltage L1-L2, utility grid | SU F1 INV9 | GriMs_V_PhsAB_F | V | 30.5.1561
SUF1INV9 | 89 | Line-to-line voltage L2-L3, utility grid | SU F1 INV9 | GriMs_V_PhsBC_F | V | 30.5.1562
SUF1INV9 | 90 | Line-to-line voltage L3-L1, utility grid | SU F1 INV9 | GriMs_V_PhsCA_F | V | 30.5.1563
SUF1INV9 | 91 | Power frequency | SU F1 INV9 | GriMs_Hz_F | Hz | 30.5.1564
SUF1INV9 | 92 | Temperature in the AC range | SU F1 INV9 | TmpCab_Acc_F | °C | 30.5.1565
SUF1INV9 | 93 | Temperature in the DC range | SU F1 INV9 | TmpCab_Dcc_F | °C | 30.5.1566
SUF1INV9 | 94 | Temperature in the electronics area | SU F1 INV9 | TmpCab_Rio_F | °C | 30.5.1567
SUF1INV9 | 95 | Temperature in interior, maximum value | SU F1 INV9 | TmpCab_Max_F | °C | 30.5.1568
SUF1INV9 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F1 INV9 | TmpStk_IgbtMax_F | °C | 30.5.1569
SUF1INV9 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F1 INV9 | TmpStk_PcbMax_F | °C | 30.5.1570
SUF1INV9 | 98 | Outside temperature | SU F1 INV9 | TmpExl_F | ?C | 30.5.1571
SUF1INV9 | 99 | Temperature of the MV transformer | SU F1 INV9 | TmpTrf_F | °C | 30.5.1572
SUF1INV9 | 100 | Temperature of inverter bridge 1 (switch) | SU F1 INV9 | TmpStk1_Igbt_F | °C | 30.5.1573
SUF1INV9 | 101 | Temperature of inverter bridge 2 (switch) | SU F1 INV9 | TmpStk2_Igbt_F | °C | 30.5.1574
SUF1INV9 | 102 | Temperature of inverter bridge 3 (switch) | SU F1 INV9 | TmpStk3_Igbt_F | °C | 30.5.1575
SUF1INV9 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F1 INV9 | TmpStk1_Pcb_F | ?C | 30.5.1576
SUF1INV9 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F1 INV9 | TmpStk2_Pcb_F | ?C | 30.5.1577
SUF1INV9 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F1 INV9 | TmpStk3_Pcb_F | ?C | 30.5.1578
SUF1INV9 | 106 | MV transformer pressure | SU F1 INV9 | PresTrf_F | "-" | 30.5.1579
SUF1INV9 | 110 | Switching status of the DC load-break switch | SU F1 INV9 | DcSwStt | "-" | 30.5.1580
SUINV9JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV9 | Dat_UpdCnt_1 | "-" | 30.5.1581
SUINV9JB1 | 2 | DC current input 1 | SU F1 INV9 | DcMs_Amp_01 | A | 30.5.1582
SUINV9JB1 | 3 | DC current input 2 | SU F1 INV9 | DcMs_Amp_02 | A | 30.5.1583
SUINV9JB1 | 4 | DC current input 3 | SU F1 INV9 | DcMs_Amp_03 | A | 30.5.1584
SUINV9JB1 | 5 | DC current input 4 | SU F1 INV9 | DcMs_Amp_04 | A | 30.5.1585
SUINV9JB1 | 6 | DC current input 5 | SU F1 INV9 | DcMs_Amp_05 | A | 30.5.1586
SUINV9JB1 | 7 | DC current input 6 | SU F1 INV9 | DcMs_Amp_06 | A | 30.5.1587
SUINV9JB1 | 8 | DC current input 7 | SU F1 INV9 | DcMs_Amp_07 | A | 30.5.1588
SUINV9JB1 | 9 | DC current input 8 | SU F1 INV9 | DcMs_Amp_08 | A | 30.5.1589
SUINV9JB1 | 10 | DC current input 9 | SU F1 INV9 | DcMs_Amp_09 | A | 30.5.1590
SUINV9JB1 | 11 | DC current input 10 | SU F1 INV9 | DcMs_Amp_10 | A | 30.5.1591
SUINV9JB1 | 12 | DC current input 11 | SU F1 INV9 | DcMs_Amp_11 | A | 30.5.1592
SUINV9JB1 | 13 | DC current input 12 | SU F1 INV9 | DcMs_Amp_12 | A | 30.5.1593
SUINV9JB1 | 14 | DC current input 13 | SU F1 INV9 | DcMs_Amp_13 | A | 30.5.1594
SUINV9JB1 | 15 | DC current input 14 | SU F1 INV9 | DcMs_Amp_14 | A | 30.5.1595
SUINV9JB1 | 16 | DC current input 15 | SU F1 INV9 | DcMs_Amp_15 | A | 30.5.1596
SUINV9JB1 | 17 | DC current input 16 | SU F1 INV9 | DcMs_Amp_16 | A | 30.5.1597
SUINV9JB1 | 18 | DC current input 1 | SU F1 INV9 | DcMs_Amp_01_F | A | 30.5.1598
SUINV9JB1 | 19 | DC current input 2 | SU F1 INV9 | DcMs_Amp_02_F | A | 30.5.1599
SUINV9JB1 | 20 | DC current input 3 | SU F1 INV9 | DcMs_Amp_03_F | A | 30.5.1600
SUINV9JB1 | 21 | DC current input 4 | SU F1 INV9 | DcMs_Amp_04_F | A | 30.5.1601
SUINV9JB1 | 22 | DC current input 5 | SU F1 INV9 | DcMs_Amp_05_F | A | 30.5.1602
SUINV9JB1 | 23 | DC current input 6 | SU F1 INV9 | DcMs_Amp_06_F | A | 30.5.1603
SUINV9JB1 | 24 | DC current input 7 | SU F1 INV9 | DcMs_Amp_07_F | A | 30.5.1604
SUINV9JB1 | 25 | DC current input 8 | SU F1 INV9 | DcMs_Amp_08_F | A | 30.5.1605
SUINV9JB1 | 26 | DC current input 9 | SU F1 INV9 | DcMs_Amp_09_F | A | 30.5.1606
SUINV9JB1 | 27 | DC current input 10 | SU F1 INV9 | DcMs_Amp_10_F | A | 30.5.1607
SUINV9JB1 | 28 | DC current input 11 | SU F1 INV9 | DcMs_Amp_11_F | A | 30.5.1608
SUINV9JB1 | 29 | DC current input 12 | SU F1 INV9 | DcMs_Amp_12_F | A | 30.5.1609
SUINV9JB1 | 30 | DC current input 13 | SU F1 INV9 | DcMs_Amp_13_F | A | 30.5.1610
SUINV9JB1 | 31 | DC current input 14 | SU F1 INV9 | DcMs_Amp_14_F | A | 30.5.1611
SUINV9JB1 | 32 | DC current input 15 | SU F1 INV9 | DcMs_Amp_15_F | A | 30.5.1612
SUINV9JB1 | 33 | DC current input 16 | SU F1 INV9 | DcMs_Amp_16_F | A | 30.5.1613
SUINV9JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F1 INV9 | Dat_UpdCnt_1 | "-" | 30.5.1614
SUINV9JB2 | 2 | DC current input 1 | SU F1 INV9 | DcMs_Amp_01 | A | 30.5.1615
SUINV9JB2 | 3 | DC current input 2 | SU F1 INV9 | DcMs_Amp_02 | A | 30.5.1616
SUINV9JB2 | 4 | DC current input 3 | SU F1 INV9 | DcMs_Amp_03 | A | 30.5.1617
SUINV9JB2 | 5 | DC current input 4 | SU F1 INV9 | DcMs_Amp_04 | A | 30.5.1618
SUINV9JB2 | 6 | DC current input 5 | SU F1 INV9 | DcMs_Amp_05 | A | 30.5.1619
SUINV9JB2 | 7 | DC current input 6 | SU F1 INV9 | DcMs_Amp_06 | A | 30.5.1620
SUINV9JB2 | 8 | DC current input 7 | SU F1 INV9 | DcMs_Amp_07 | A | 30.5.1621
SUINV9JB2 | 9 | DC current input 8 | SU F1 INV9 | DcMs_Amp_08 | A | 30.5.1622
SUINV9JB2 | 10 | DC current input 9 | SU F1 INV9 | DcMs_Amp_09 | A | 30.5.1623
SUINV9JB2 | 11 | DC current input 10 | SU F1 INV9 | DcMs_Amp_10 | A | 30.5.1624
SUINV9JB2 | 12 | DC current input 11 | SU F1 INV9 | DcMs_Amp_11 | A | 30.5.1625
SUINV9JB2 | 13 | DC current input 12 | SU F1 INV9 | DcMs_Amp_12 | A | 30.5.1626
SUINV9JB2 | 14 | DC current input 13 | SU F1 INV9 | DcMs_Amp_13 | A | 30.5.1627
SUINV9JB2 | 15 | DC current input 14 | SU F1 INV9 | DcMs_Amp_14 | A | 30.5.1628
SUINV9JB2 | 16 | DC current input 15 | SU F1 INV9 | DcMs_Amp_15 | A | 30.5.1629
SUINV9JB2 | 17 | DC current input 16 | SU F1 INV9 | DcMs_Amp_16 | A | 30.5.1630
SUINV9JB2 | 18 | DC current input 1 | SU F1 INV9 | DcMs_Amp_01_F | A | 30.5.1631
SUINV9JB2 | 19 | DC current input 2 | SU F1 INV9 | DcMs_Amp_02_F | A | 30.5.1632
SUINV9JB2 | 20 | DC current input 3 | SU F1 INV9 | DcMs_Amp_03_F | A | 30.5.1633
SUINV9JB2 | 21 | DC current input 4 | SU F1 INV9 | DcMs_Amp_04_F | A | 30.5.1634
SUINV9JB2 | 22 | DC current input 5 | SU F1 INV9 | DcMs_Amp_05_F | A | 30.5.1635
SUINV9JB2 | 23 | DC current input 6 | SU F1 INV9 | DcMs_Amp_06_F | A | 30.5.1636
SUINV9JB2 | 24 | DC current input 7 | SU F1 INV9 | DcMs_Amp_07_F | A | 30.5.1637
SUINV9JB2 | 25 | DC current input 8 | SU F1 INV9 | DcMs_Amp_08_F | A | 30.5.1638
SUINV9JB2 | 26 | DC current input 9 | SU F1 INV9 | DcMs_Amp_09_F | A | 30.5.1639
SUINV9JB2 | 27 | DC current input 10 | SU F1 INV9 | DcMs_Amp_10_F | A | 30.5.1640
SUINV9JB2 | 28 | DC current input 11 | SU F1 INV9 | DcMs_Amp_11_F | A | 30.5.1641
SUINV9JB2 | 29 | DC current input 12 | SU F1 INV9 | DcMs_Amp_12_F | A | 30.5.1642
SUINV9JB2 | 30 | DC current input 13 | SU F1 INV9 | DcMs_Amp_13_F | A | 30.5.1643
SUINV9JB2 | 31 | DC current input 14 | SU F1 INV9 | DcMs_Amp_14_F | A | 30.5.1644
SUINV9JB2 | 32 | DC current input 15 | SU F1 INV9 | DcMs_Amp_15_F | A | 30.5.1645
SUINV9JB2 | 33 | DC current input 16 | SU F1 INV9 | DcMs_Amp_16_F | A | 30.5.1646
SUF252F2 | 15 |  | SU F2 52F2 | Breaker device control block | Blocking | 30.5.1647
SUF252F2 | 18 |  | SU F2 52F2 | Cause of interlocking | Cause | 30.5.1648
SUF252F2 | 19 |  | SU F2 52F2 | Breaker selection on monitor | Sessions | 30.5.1649
SUF252F2 | 55 |  | SU F2 52F2 | Add cause of command | Add Cause | 30.5.1650
SUF252I | 131 |  | SU F2 52M | Current | A | 30.5.1651
SUF252P | 133 |  | SU F2 52M | Active Power | MW | 30.5.1652
SUF252PF | 136 |  | SU F2 52M | Power Factor | Cosfii | 30.5.1653
SUF252Q | 134 |  | SU F2 52M | Reactive Power | Mvar | 30.5.1654
SUF252V | 132 |  | SU F2 52M | Voltage | kV | 30.5.1655
SUF2 | 20 |  | SU F2 BAY | Bay blockings | Blocking | 30.5.1656
SUF2 | 21 |  | SU F2 BAY | Bay selection on monitor | Sessions | 30.5.1657
SUF2INV13 | 1 | DC voltage DC plus to DC minus | SU F2 INV13 | DcMs_Vol | V | 30.5.1658
SUF2INV13 | 2 | DC current inverter bridge 1 | SU F2 INV13 | DcMs_Amp_Stk1 | A | 30.5.1659
SUF2INV13 | 3 | DC current inverter bridge 2 | SU F2 INV13 | DcMs_Amp_Stk2 | A | 30.5.1660
SUF2INV13 | 4 | DC current inverter bridge 3 | SU F2 INV13 | DcMs_Amp_Stk3 | A | 30.5.1661
SUF2INV13 | 5 | DC current, total | SU F2 INV13 | DcMs_TotAmp | A | 30.5.1662
SUF2INV13 | 6 | DC power, total | SU F2 INV13 | DcMs_TotWatt | kW | 30.5.1663
SUF2INV13 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV13 | InvMs_DclVol_Stk1 | V | 30.5.1664
SUF2INV13 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV13 | InvMs_DclVol_Stk2 | V | 30.5.1665
SUF2INV13 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV13 | InvMs_DclVol_Stk3 | V | 30.5.1666
SUF2INV13 | 10 | AC current L1, total | SU F2 INV13 | InvMs_TotA_PhsA | A | 30.5.1667
SUF2INV13 | 11 | AC current L2, total | SU F2 INV13 | InvMs_TotA_PhsB | A | 30.5.1668
SUF2INV13 | 12 | AC current L3, total | SU F2 INV13 | InvMs_TotA_PhsC | A | 30.5.1669
SUF2INV13 | 13 | Power factor (cos phi) | SU F2 INV13 | InvMs_PF | "-" | 30.5.1670
SUF2INV13 | 14 | Apparent power, total | SU F2 INV13 | InvMs_TotVA | kVA | 30.5.1671
SUF2INV13 | 15 | Active power, total | SU F2 INV13 | InvMs_TotW | kW | 30.5.1672
SUF2INV13 | 16 | Reactive power, total | SU F2 INV13 | InvMs_TotVAr | kVAr | 30.5.1673
SUF2INV13 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV13 | GriMs_V_PhsAB | V | 30.5.1674
SUF2INV13 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV13 | GriMs_V_PhsBC | V | 30.5.1675
SUF2INV13 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV13 | GriMs_V_PhsCA | V | 30.5.1676
SUF2INV13 | 20 | Power frequency | SU F2 INV13 | GriMs_Hz | Hz | 30.5.1677
SUF2INV13 | 21 | Temperature in the AC range | SU F2 INV13 | TmpCab_Acc | °C | 30.5.1678
SUF2INV13 | 22 | Temperature in the DC range | SU F2 INV13 | TmpCab_Dcc | °C | 30.5.1679
SUF2INV13 | 23 | Temperature in the electronics area | SU F2 INV13 | TmpCab_Rio | °C | 30.5.1680
SUF2INV13 | 24 | Temperature in interior, maximum value | SU F2 INV13 | TmpCab_Max | °C | 30.5.1681
SUF2INV13 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV13 | TmpStk_IgbtMax | °C | 30.5.1682
SUF2INV13 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV13 | TmpStk_PcbMax | °C | 30.5.1683
SUF2INV13 | 27 | Outside temperature | SU F2 INV13 | TmpExl | ?C | 30.5.1684
SUF2INV13 | 28 | Temperature of the MV transformer | SU F2 INV13 | TmpTrf | °C | 30.5.1685
SUF2INV13 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV13 | DcSw1Stt | "-" | 30.5.1686
SUF2INV13 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV13 | DcSw2Stt | "-" | 30.5.1687
SUF2INV13 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV13 | DcSw3Stt | "-" | 30.5.1688
SUF2INV13 | 32 | Switching status of the AC circuit breaker | SU F2 INV13 | AcSwStt | "-" | 30.5.1689
SUF2INV13 | 33 | Switching state of the capacitor contactor | SU F2 INV13 | CapacSwStt | "-" | 30.5.1690
SUF2INV13 | 34 | Switching status of the pre-charging contactor | SU F2 INV13 | PrchrgSwStt | "-" | 30.5.1691
SUF2INV13 | 35 | Feed-in hours | SU F2 INV13 | Cnt_TotFeedTm | "-" | 30.5.1692
SUF2INV13 | 36 | Operating hours | SU F2 INV13 | Cnt_TotOpTm | "-" | 30.5.1693
SUF2INV13 | 37 | DC energy drawn, total | SU F2 INV13 | Cnt_TotWatthIn | MWh | 30.5.1694
SUF2INV13 | 38 | AC energy fed in, total | SU F2 INV13 | Cnt_TotWhOut | MWh | 30.5.1695
SUF2INV13 | 39 | DC energy drawn that day | SU F2 INV13 | Cnt_WatthIn | MWh | 30.5.1696
SUF2INV13 | 40 | AC energy fed in that day | SU F2 INV13 | Cnt_WhOut | MWh | 30.5.1697
SUF2INV13 | 41 | Operating hours of the interior fan 1 | SU F2 INV13 | Cnt_FanCab1Tm | "-" | 30.5.1698
SUF2INV13 | 42 | Operating hours of the interior fan 2 | SU F2 INV13 | Cnt_FanCab2Tm | "-" | 30.5.1699
SUF2INV13 | 43 | Operating hours of the inverter bridge fan | SU F2 INV13 | Cnt_FanStkTm | "-" | 30.5.1700
SUF2INV13 | 44 | Operating hours of the internal heating element | SU F2 INV13 | Cnt_HtCabTm | "-" | 30.5.1701
SUF2INV13 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV13 | Cnt_HtLoExlTmpTm | "-" | 30.5.1702
SUF2INV13 | 46 | Error location of the present error | SU F2 INV13 | ErrLcn | "-" | 30.5.1703
SUF2INV13 | 47 | Error status of the inverter | SU F2 INV13 | ErrStt | "-" | 30.5.1704
SUF2INV13 | 48 | Error number of the present error | SU F2 INV13 | ErrNo | "-" | 30.5.1705
SUF2INV13 | 49 | Operating state of the inverter | SU F2 INV13 | OpStt | "-" | 30.5.1706
SUF2INV13 | 50 | Switch status of the start-stop key switch | SU F2 INV13 | Rio_KeySw | "-" | 30.5.1707
SUF2INV13 | 51 | Waiting time for grid connection | SU F2 INV13 | WaitGriTm | s | 30.5.1708
SUF2INV13 | 52 | Inverter serial number | SU F2 INV13 | DevInf_SerNo | "-" | 30.5.1709
SUF2INV13 | 53 | Switching status of the GFDI | SU F2 INV13 | GfdiSwStt | "-" | 30.5.1710
SUF2INV13 | 54 | Active power, setpoint | SU F2 INV13 | WSpt | kW | 30.5.1711
SUF2INV13 | 55 | Maximum apparent power, setpoint | SU F2 INV13 | VAMaxSpt | kVA | 30.5.1712
SUF2INV13 | 56 | Reactive power, setpoint | SU F2 INV13 | VArSpt | kVAr | 30.5.1713
SUF2INV13 | 57 | Power factor cos (phi), setpoint | SU F2 INV13 | PFSpt | "-" | 30.5.1714
SUF2INV13 | 58 | Fast stop hermetic protection, pressure | SU F2 INV13 | TrfPro_Pres | "-" | 30.5.1715
SUF2INV13 | 59 | Fast stop hermetic protection, temperature | SU F2 INV13 | TrfPro_TmpTrp | "-" | 30.5.1716
SUF2INV13 | 60 | Hermetic protection, gas fill level | SU F2 INV13 | TrfPro_GasOilLev | "-" | 30.5.1717
SUF2INV13 | 61 | Hermetic pressure, temperature warning | SU F2 INV13 | TrfPro_TmpWrn | "-" | 30.5.1718
SUF2INV13 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV13 | TmpStk1_Igbt | °C | 30.5.1719
SUF2INV13 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV13 | TmpStk2_Igbt | °C | 30.5.1720
SUF2INV13 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV13 | TmpStk3_Igbt | °C | 30.5.1721
SUF2INV13 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV13 | TmpStk1_Pcb | ?C | 30.5.1722
SUF2INV13 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV13 | TmpStk2_Pcb | ?C | 30.5.1723
SUF2INV13 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV13 | TmpStk3_Pcb | ?C | 30.5.1724
SUF2INV13 | 68 | AC Energy Fed in the previous Day | SU F2 INV13 | Cnt_YstdWhOut | MWh | 30.5.1725
SUF2INV13 | 69 | CPU running time since system start | SU F2 INV13 | Cpu1UpTime | s | 30.5.1726
SUF2INV13 | 70 | Insulation resistance | SU F2 INV13 | PvGnd_RisIso | kOhm | 30.5.1727
SUF2INV13 | 71 | MV transformer pressure | SU F2 INV13 | PresTrf | "-" | 30.5.1728
SUF2INV13 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV13 | PresTrf_ErrStt | "-" | 30.5.1729
SUF2INV13 | 73 | DC voltage DC plus to DC minus | SU F2 INV13 | DcMs_Vol_F | V | 30.5.1730
SUF2INV13 | 74 | DC current inverter bridge 1 | SU F2 INV13 | DcMs_Amp_Stk1_F | A | 30.5.1731
SUF2INV13 | 75 | DC current inverter bridge 2 | SU F2 INV13 | DcMs_Amp_Stk2_F | A | 30.5.1732
SUF2INV13 | 76 | DC current inverter bridge 3 | SU F2 INV13 | DcMs_Amp_Stk3_F | A | 30.5.1733
SUF2INV13 | 77 | DC current, total | SU F2 INV13 | DcMs_TotAmp_F | A | 30.5.1734
SUF2INV13 | 78 | DC power, total | SU F2 INV13 | DcMs_TotWatt_F | kW | 30.5.1735
SUF2INV13 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV13 | InvMs_DclVol_Stk1_F | V | 30.5.1736
SUF2INV13 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV13 | InvMs_DclVol_Stk2_F | V | 30.5.1737
SUF2INV13 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV13 | InvMs_DclVol_Stk3_F | V | 30.5.1738
SUF2INV13 | 82 | AC current L1, total | SU F2 INV13 | InvMs_TotA_PhsA_F | A | 30.5.1739
SUF2INV13 | 83 | AC current L2, total | SU F2 INV13 | InvMs_TotA_PhsB_F | A | 30.5.1740
SUF2INV13 | 84 | AC current L3, total | SU F2 INV13 | InvMs_TotA_PhsC_F | A | 30.5.1741
SUF2INV13 | 85 | Power factor (cos phi) | SU F2 INV13 | InvMs_PF_F | "-" | 30.5.1742
SUF2INV13 | 86 | Active power, total | SU F2 INV13 | InvMs_TotW_F | kW | 30.5.1743
SUF2INV13 | 87 | Reactive power, total | SU F2 INV13 | InvMs_TotVAr_F | kVAr | 30.5.1744
SUF2INV13 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV13 | GriMs_V_PhsAB_F | V | 30.5.1745
SUF2INV13 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV13 | GriMs_V_PhsBC_F | V | 30.5.1746
SUF2INV13 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV13 | GriMs_V_PhsCA_F | V | 30.5.1747
SUF2INV13 | 91 | Power frequency | SU F2 INV13 | GriMs_Hz_F | Hz | 30.5.1748
SUF2INV13 | 92 | Temperature in the AC range | SU F2 INV13 | TmpCab_Acc_F | °C | 30.5.1749
SUF2INV13 | 93 | Temperature in the DC range | SU F2 INV13 | TmpCab_Dcc_F | °C | 30.5.1750
SUF2INV13 | 94 | Temperature in the electronics area | SU F2 INV13 | TmpCab_Rio_F | °C | 30.5.1751
SUF2INV13 | 95 | Temperature in interior, maximum value | SU F2 INV13 | TmpCab_Max_F | °C | 30.5.1752
SUF2INV13 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV13 | TmpStk_IgbtMax_F | °C | 30.5.1753
SUF2INV13 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV13 | TmpStk_PcbMax_F | °C | 30.5.1754
SUF2INV13 | 98 | Outside temperature | SU F2 INV13 | TmpExl_F | ?C | 30.5.1755
SUF2INV13 | 99 | Temperature of the MV transformer | SU F2 INV13 | TmpTrf_F | °C | 30.5.1756
SUF2INV13 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV13 | TmpStk1_Igbt_F | °C | 30.5.1757
SUF2INV13 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV13 | TmpStk2_Igbt_F | °C | 30.5.1758
SUF2INV13 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV13 | TmpStk3_Igbt_F | °C | 30.5.1759
SUF2INV13 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV13 | TmpStk1_Pcb_F | ?C | 30.5.1760
SUF2INV13 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV13 | TmpStk2_Pcb_F | ?C | 30.5.1761
SUF2INV13 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV13 | TmpStk3_Pcb_F | ?C | 30.5.1762
SUF2INV13 | 106 | MV transformer pressure | SU F2 INV13 | PresTrf_F | "-" | 30.5.1763
SUF2INV13 | 110 | Switching status of the DC load-break switch | SU F2 INV13 | DcSwStt | "-" | 30.5.1764
SUINV13JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV13 | Dat_UpdCnt_1 | "-" | 30.5.1765
SUINV13JB1 | 2 | DC current input 1 | SU F2 INV13 | DcMs_Amp_01 | A | 30.5.1766
SUINV13JB1 | 3 | DC current input 2 | SU F2 INV13 | DcMs_Amp_02 | A | 30.5.1767
SUINV13JB1 | 4 | DC current input 3 | SU F2 INV13 | DcMs_Amp_03 | A | 30.5.1768
SUINV13JB1 | 5 | DC current input 4 | SU F2 INV13 | DcMs_Amp_04 | A | 30.5.1769
SUINV13JB1 | 6 | DC current input 5 | SU F2 INV13 | DcMs_Amp_05 | A | 30.5.1770
SUINV13JB1 | 7 | DC current input 6 | SU F2 INV13 | DcMs_Amp_06 | A | 30.5.1771
SUINV13JB1 | 8 | DC current input 7 | SU F2 INV13 | DcMs_Amp_07 | A | 30.5.1772
SUINV13JB1 | 9 | DC current input 8 | SU F2 INV13 | DcMs_Amp_08 | A | 30.5.1773
SUINV13JB1 | 10 | DC current input 9 | SU F2 INV13 | DcMs_Amp_09 | A | 30.5.1774
SUINV13JB1 | 11 | DC current input 10 | SU F2 INV13 | DcMs_Amp_10 | A | 30.5.1775
SUINV13JB1 | 12 | DC current input 11 | SU F2 INV13 | DcMs_Amp_11 | A | 30.5.1776
SUINV13JB1 | 13 | DC current input 12 | SU F2 INV13 | DcMs_Amp_12 | A | 30.5.1777
SUINV13JB1 | 14 | DC current input 13 | SU F2 INV13 | DcMs_Amp_13 | A | 30.5.1778
SUINV13JB1 | 15 | DC current input 14 | SU F2 INV13 | DcMs_Amp_14 | A | 30.5.1779
SUINV13JB1 | 16 | DC current input 15 | SU F2 INV13 | DcMs_Amp_15 | A | 30.5.1780
SUINV13JB1 | 17 | DC current input 16 | SU F2 INV13 | DcMs_Amp_16 | A | 30.5.1781
SUINV13JB1 | 18 | DC current input 1 | SU F2 INV13 | DcMs_Amp_01_F | A | 30.5.1782
SUINV13JB1 | 19 | DC current input 2 | SU F2 INV13 | DcMs_Amp_02_F | A | 30.5.1783
SUINV13JB1 | 20 | DC current input 3 | SU F2 INV13 | DcMs_Amp_03_F | A | 30.5.1784
SUINV13JB1 | 21 | DC current input 4 | SU F2 INV13 | DcMs_Amp_04_F | A | 30.5.1785
SUINV13JB1 | 22 | DC current input 5 | SU F2 INV13 | DcMs_Amp_05_F | A | 30.5.1786
SUINV13JB1 | 23 | DC current input 6 | SU F2 INV13 | DcMs_Amp_06_F | A | 30.5.1787
SUINV13JB1 | 24 | DC current input 7 | SU F2 INV13 | DcMs_Amp_07_F | A | 30.5.1788
SUINV13JB1 | 25 | DC current input 8 | SU F2 INV13 | DcMs_Amp_08_F | A | 30.5.1789
SUINV13JB1 | 26 | DC current input 9 | SU F2 INV13 | DcMs_Amp_09_F | A | 30.5.1790
SUINV13JB1 | 27 | DC current input 10 | SU F2 INV13 | DcMs_Amp_10_F | A | 30.5.1791
SUINV13JB1 | 28 | DC current input 11 | SU F2 INV13 | DcMs_Amp_11_F | A | 30.5.1792
SUINV13JB1 | 29 | DC current input 12 | SU F2 INV13 | DcMs_Amp_12_F | A | 30.5.1793
SUINV13JB1 | 30 | DC current input 13 | SU F2 INV13 | DcMs_Amp_13_F | A | 30.5.1794
SUINV13JB1 | 31 | DC current input 14 | SU F2 INV13 | DcMs_Amp_14_F | A | 30.5.1795
SUINV13JB1 | 32 | DC current input 15 | SU F2 INV13 | DcMs_Amp_15_F | A | 30.5.1796
SUINV13JB1 | 33 | DC current input 16 | SU F2 INV13 | DcMs_Amp_16_F | A | 30.5.1797
SUINV13JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV13 | Dat_UpdCnt_1 | "-" | 30.5.1798
SUINV13JB2 | 2 | DC current input 1 | SU F2 INV13 | DcMs_Amp_01 | A | 30.5.1799
SUINV13JB2 | 3 | DC current input 2 | SU F2 INV13 | DcMs_Amp_02 | A | 30.5.1800
SUINV13JB2 | 4 | DC current input 3 | SU F2 INV13 | DcMs_Amp_03 | A | 30.5.1801
SUINV13JB2 | 5 | DC current input 4 | SU F2 INV13 | DcMs_Amp_04 | A | 30.5.1802
SUINV13JB2 | 6 | DC current input 5 | SU F2 INV13 | DcMs_Amp_05 | A | 30.5.1803
SUINV13JB2 | 7 | DC current input 6 | SU F2 INV13 | DcMs_Amp_06 | A | 30.5.1804
SUINV13JB2 | 8 | DC current input 7 | SU F2 INV13 | DcMs_Amp_07 | A | 30.5.1805
SUINV13JB2 | 9 | DC current input 8 | SU F2 INV13 | DcMs_Amp_08 | A | 30.5.1806
SUINV13JB2 | 10 | DC current input 9 | SU F2 INV13 | DcMs_Amp_09 | A | 30.5.1807
SUINV13JB2 | 11 | DC current input 10 | SU F2 INV13 | DcMs_Amp_10 | A | 30.5.1808
SUINV13JB2 | 12 | DC current input 11 | SU F2 INV13 | DcMs_Amp_11 | A | 30.5.1809
SUINV13JB2 | 13 | DC current input 12 | SU F2 INV13 | DcMs_Amp_12 | A | 30.5.1810
SUINV13JB2 | 14 | DC current input 13 | SU F2 INV13 | DcMs_Amp_13 | A | 30.5.1811
SUINV13JB2 | 15 | DC current input 14 | SU F2 INV13 | DcMs_Amp_14 | A | 30.5.1812
SUINV13JB2 | 16 | DC current input 15 | SU F2 INV13 | DcMs_Amp_15 | A | 30.5.1813
SUINV13JB2 | 17 | DC current input 16 | SU F2 INV13 | DcMs_Amp_16 | A | 30.5.1814
SUINV13JB2 | 18 | DC current input 1 | SU F2 INV13 | DcMs_Amp_01_F | A | 30.5.1815
SUINV13JB2 | 19 | DC current input 2 | SU F2 INV13 | DcMs_Amp_02_F | A | 30.5.1816
SUINV13JB2 | 20 | DC current input 3 | SU F2 INV13 | DcMs_Amp_03_F | A | 30.5.1817
SUINV13JB2 | 21 | DC current input 4 | SU F2 INV13 | DcMs_Amp_04_F | A | 30.5.1818
SUINV13JB2 | 22 | DC current input 5 | SU F2 INV13 | DcMs_Amp_05_F | A | 30.5.1819
SUINV13JB2 | 23 | DC current input 6 | SU F2 INV13 | DcMs_Amp_06_F | A | 30.5.1820
SUINV13JB2 | 24 | DC current input 7 | SU F2 INV13 | DcMs_Amp_07_F | A | 30.5.1821
SUINV13JB2 | 25 | DC current input 8 | SU F2 INV13 | DcMs_Amp_08_F | A | 30.5.1822
SUINV13JB2 | 26 | DC current input 9 | SU F2 INV13 | DcMs_Amp_09_F | A | 30.5.1823
SUINV13JB2 | 27 | DC current input 10 | SU F2 INV13 | DcMs_Amp_10_F | A | 30.5.1824
SUINV13JB2 | 28 | DC current input 11 | SU F2 INV13 | DcMs_Amp_11_F | A | 30.5.1825
SUINV13JB2 | 29 | DC current input 12 | SU F2 INV13 | DcMs_Amp_12_F | A | 30.5.1826
SUINV13JB2 | 30 | DC current input 13 | SU F2 INV13 | DcMs_Amp_13_F | A | 30.5.1827
SUINV13JB2 | 31 | DC current input 14 | SU F2 INV13 | DcMs_Amp_14_F | A | 30.5.1828
SUINV13JB2 | 32 | DC current input 15 | SU F2 INV13 | DcMs_Amp_15_F | A | 30.5.1829
SUINV13JB2 | 33 | DC current input 16 | SU F2 INV13 | DcMs_Amp_16_F | A | 30.5.1830
SUF2INV15 | 1 | DC voltage DC plus to DC minus | SU F2 INV15 | DcMs_Vol | V | 30.5.1831
SUF2INV15 | 2 | DC current inverter bridge 1 | SU F2 INV15 | DcMs_Amp_Stk1 | A | 30.5.1832
SUF2INV15 | 3 | DC current inverter bridge 2 | SU F2 INV15 | DcMs_Amp_Stk2 | A | 30.5.1833
SUF2INV15 | 4 | DC current inverter bridge 3 | SU F2 INV15 | DcMs_Amp_Stk3 | A | 30.5.1834
SUF2INV15 | 5 | DC current, total | SU F2 INV15 | DcMs_TotAmp | A | 30.5.1835
SUF2INV15 | 6 | DC power, total | SU F2 INV15 | DcMs_TotWatt | kW | 30.5.1836
SUF2INV15 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV15 | InvMs_DclVol_Stk1 | V | 30.5.1837
SUF2INV15 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV15 | InvMs_DclVol_Stk2 | V | 30.5.1838
SUF2INV15 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV15 | InvMs_DclVol_Stk3 | V | 30.5.1839
SUF2INV15 | 10 | AC current L1, total | SU F2 INV15 | InvMs_TotA_PhsA | A | 30.5.1840
SUF2INV15 | 11 | AC current L2, total | SU F2 INV15 | InvMs_TotA_PhsB | A | 30.5.1841
SUF2INV15 | 12 | AC current L3, total | SU F2 INV15 | InvMs_TotA_PhsC | A | 30.5.1842
SUF2INV15 | 13 | Power factor (cos phi) | SU F2 INV15 | InvMs_PF | "-" | 30.5.1843
SUF2INV15 | 14 | Apparent power, total | SU F2 INV15 | InvMs_TotVA | kVA | 30.5.1844
SUF2INV15 | 15 | Active power, total | SU F2 INV15 | InvMs_TotW | kW | 30.5.1845
SUF2INV15 | 16 | Reactive power, total | SU F2 INV15 | InvMs_TotVAr | kVAr | 30.5.1846
SUF2INV15 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV15 | GriMs_V_PhsAB | V | 30.5.1847
SUF2INV15 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV15 | GriMs_V_PhsBC | V | 30.5.1848
SUF2INV15 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV15 | GriMs_V_PhsCA | V | 30.5.1849
SUF2INV15 | 20 | Power frequency | SU F2 INV15 | GriMs_Hz | Hz | 30.5.1850
SUF2INV15 | 21 | Temperature in the AC range | SU F2 INV15 | TmpCab_Acc | °C | 30.5.1851
SUF2INV15 | 22 | Temperature in the DC range | SU F2 INV15 | TmpCab_Dcc | °C | 30.5.1852
SUF2INV15 | 23 | Temperature in the electronics area | SU F2 INV15 | TmpCab_Rio | °C | 30.5.1853
SUF2INV15 | 24 | Temperature in interior, maximum value | SU F2 INV15 | TmpCab_Max | °C | 30.5.1854
SUF2INV15 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV15 | TmpStk_IgbtMax | °C | 30.5.1855
SUF2INV15 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV15 | TmpStk_PcbMax | °C | 30.5.1856
SUF2INV15 | 27 | Outside temperature | SU F2 INV15 | TmpExl | ?C | 30.5.1857
SUF2INV15 | 28 | Temperature of the MV transformer | SU F2 INV15 | TmpTrf | °C | 30.5.1858
SUF2INV15 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV15 | DcSw1Stt | "-" | 30.5.1859
SUF2INV15 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV15 | DcSw2Stt | "-" | 30.5.1860
SUF2INV15 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV15 | DcSw3Stt | "-" | 30.5.1861
SUF2INV15 | 32 | Switching status of the AC circuit breaker | SU F2 INV15 | AcSwStt | "-" | 30.5.1862
SUF2INV15 | 33 | Switching state of the capacitor contactor | SU F2 INV15 | CapacSwStt | "-" | 30.5.1863
SUF2INV15 | 34 | Switching status of the pre-charging contactor | SU F2 INV15 | PrchrgSwStt | "-" | 30.5.1864
SUF2INV15 | 35 | Feed-in hours | SU F2 INV15 | Cnt_TotFeedTm | "-" | 30.5.1865
SUF2INV15 | 36 | Operating hours | SU F2 INV15 | Cnt_TotOpTm | "-" | 30.5.1866
SUF2INV15 | 37 | DC energy drawn, total | SU F2 INV15 | Cnt_TotWatthIn | MWh | 30.5.1867
SUF2INV15 | 38 | AC energy fed in, total | SU F2 INV15 | Cnt_TotWhOut | MWh | 30.5.1868
SUF2INV15 | 39 | DC energy drawn that day | SU F2 INV15 | Cnt_WatthIn | MWh | 30.5.1869
SUF2INV15 | 40 | AC energy fed in that day | SU F2 INV15 | Cnt_WhOut | MWh | 30.5.1870
SUF2INV15 | 41 | Operating hours of the interior fan 1 | SU F2 INV15 | Cnt_FanCab1Tm | "-" | 30.5.1871
SUF2INV15 | 42 | Operating hours of the interior fan 2 | SU F2 INV15 | Cnt_FanCab2Tm | "-" | 30.5.1872
SUF2INV15 | 43 | Operating hours of the inverter bridge fan | SU F2 INV15 | Cnt_FanStkTm | "-" | 30.5.1873
SUF2INV15 | 44 | Operating hours of the internal heating element | SU F2 INV15 | Cnt_HtCabTm | "-" | 30.5.1874
SUF2INV15 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV15 | Cnt_HtLoExlTmpTm | "-" | 30.5.1875
SUF2INV15 | 46 | Error location of the present error | SU F2 INV15 | ErrLcn | "-" | 30.5.1876
SUF2INV15 | 47 | Error status of the inverter | SU F2 INV15 | ErrStt | "-" | 30.5.1877
SUF2INV15 | 48 | Error number of the present error | SU F2 INV15 | ErrNo | "-" | 30.5.1878
SUF2INV15 | 49 | Operating state of the inverter | SU F2 INV15 | OpStt | "-" | 30.5.1879
SUF2INV15 | 50 | Switch status of the start-stop key switch | SU F2 INV15 | Rio_KeySw | "-" | 30.5.1880
SUF2INV15 | 51 | Waiting time for grid connection | SU F2 INV15 | WaitGriTm | s | 30.5.1881
SUF2INV15 | 52 | Inverter serial number | SU F2 INV15 | DevInf_SerNo | "-" | 30.5.1882
SUF2INV15 | 53 | Switching status of the GFDI | SU F2 INV15 | GfdiSwStt | "-" | 30.5.1883
SUF2INV15 | 54 | Active power, setpoint | SU F2 INV15 | WSpt | kW | 30.5.1884
SUF2INV15 | 55 | Maximum apparent power, setpoint | SU F2 INV15 | VAMaxSpt | kVA | 30.5.1885
SUF2INV15 | 56 | Reactive power, setpoint | SU F2 INV15 | VArSpt | kVAr | 30.5.1886
SUF2INV15 | 57 | Power factor cos (phi), setpoint | SU F2 INV15 | PFSpt | "-" | 30.5.1887
SUF2INV15 | 58 | Fast stop hermetic protection, pressure | SU F2 INV15 | TrfPro_Pres | "-" | 30.5.1888
SUF2INV15 | 59 | Fast stop hermetic protection, temperature | SU F2 INV15 | TrfPro_TmpTrp | "-" | 30.5.1889
SUF2INV15 | 60 | Hermetic protection, gas fill level | SU F2 INV15 | TrfPro_GasOilLev | "-" | 30.5.1890
SUF2INV15 | 61 | Hermetic pressure, temperature warning | SU F2 INV15 | TrfPro_TmpWrn | "-" | 30.5.1891
SUF2INV15 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV15 | TmpStk1_Igbt | °C | 30.5.1892
SUF2INV15 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV15 | TmpStk2_Igbt | °C | 30.5.1893
SUF2INV15 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV15 | TmpStk3_Igbt | °C | 30.5.1894
SUF2INV15 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV15 | TmpStk1_Pcb | ?C | 30.5.1895
SUF2INV15 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV15 | TmpStk2_Pcb | ?C | 30.5.1896
SUF2INV15 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV15 | TmpStk3_Pcb | ?C | 30.5.1897
SUF2INV15 | 68 | AC Energy Fed in the previous Day | SU F2 INV15 | Cnt_YstdWhOut | MWh | 30.5.1898
SUF2INV15 | 69 | CPU running time since system start | SU F2 INV15 | Cpu1UpTime | s | 30.5.1899
SUF2INV15 | 70 | Insulation resistance | SU F2 INV15 | PvGnd_RisIso | kOhm | 30.5.1900
SUF2INV15 | 71 | MV transformer pressure | SU F2 INV15 | PresTrf | "-" | 30.5.1901
SUF2INV15 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV15 | PresTrf_ErrStt | "-" | 30.5.1902
SUF2INV15 | 73 | DC voltage DC plus to DC minus | SU F2 INV15 | DcMs_Vol_F | V | 30.5.1903
SUF2INV15 | 74 | DC current inverter bridge 1 | SU F2 INV15 | DcMs_Amp_Stk1_F | A | 30.5.1904
SUF2INV15 | 75 | DC current inverter bridge 2 | SU F2 INV15 | DcMs_Amp_Stk2_F | A | 30.5.1905
SUF2INV15 | 76 | DC current inverter bridge 3 | SU F2 INV15 | DcMs_Amp_Stk3_F | A | 30.5.1906
SUF2INV15 | 77 | DC current, total | SU F2 INV15 | DcMs_TotAmp_F | A | 30.5.1907
SUF2INV15 | 78 | DC power, total | SU F2 INV15 | DcMs_TotWatt_F | kW | 30.5.1908
SUF2INV15 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV15 | InvMs_DclVol_Stk1_F | V | 30.5.1909
SUF2INV15 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV15 | InvMs_DclVol_Stk2_F | V | 30.5.1910
SUF2INV15 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV15 | InvMs_DclVol_Stk3_F | V | 30.5.1911
SUF2INV15 | 82 | AC current L1, total | SU F2 INV15 | InvMs_TotA_PhsA_F | A | 30.5.1912
SUF2INV15 | 83 | AC current L2, total | SU F2 INV15 | InvMs_TotA_PhsB_F | A | 30.5.1913
SUF2INV15 | 84 | AC current L3, total | SU F2 INV15 | InvMs_TotA_PhsC_F | A | 30.5.1914
SUF2INV15 | 85 | Power factor (cos phi) | SU F2 INV15 | InvMs_PF_F | "-" | 30.5.1915
SUF2INV15 | 86 | Active power, total | SU F2 INV15 | InvMs_TotW_F | kW | 30.5.1916
SUF2INV15 | 87 | Reactive power, total | SU F2 INV15 | InvMs_TotVAr_F | kVAr | 30.5.1917
SUF2INV15 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV15 | GriMs_V_PhsAB_F | V | 30.5.1918
SUF2INV15 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV15 | GriMs_V_PhsBC_F | V | 30.5.1919
SUF2INV15 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV15 | GriMs_V_PhsCA_F | V | 30.5.1920
SUF2INV15 | 91 | Power frequency | SU F2 INV15 | GriMs_Hz_F | Hz | 30.5.1921
SUF2INV15 | 92 | Temperature in the AC range | SU F2 INV15 | TmpCab_Acc_F | °C | 30.5.1922
SUF2INV15 | 93 | Temperature in the DC range | SU F2 INV15 | TmpCab_Dcc_F | °C | 30.5.1923
SUF2INV15 | 94 | Temperature in the electronics area | SU F2 INV15 | TmpCab_Rio_F | °C | 30.5.1924
SUF2INV15 | 95 | Temperature in interior, maximum value | SU F2 INV15 | TmpCab_Max_F | °C | 30.5.1925
SUF2INV15 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV15 | TmpStk_IgbtMax_F | °C | 30.5.1926
SUF2INV15 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV15 | TmpStk_PcbMax_F | °C | 30.5.1927
SUF2INV15 | 98 | Outside temperature | SU F2 INV15 | TmpExl_F | ?C | 30.5.1928
SUF2INV15 | 99 | Temperature of the MV transformer | SU F2 INV15 | TmpTrf_F | °C | 30.5.1929
SUF2INV15 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV15 | TmpStk1_Igbt_F | °C | 30.5.1930
SUF2INV15 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV15 | TmpStk2_Igbt_F | °C | 30.5.1931
SUF2INV15 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV15 | TmpStk3_Igbt_F | °C | 30.5.1932
SUF2INV15 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV15 | TmpStk1_Pcb_F | ?C | 30.5.1933
SUF2INV15 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV15 | TmpStk2_Pcb_F | ?C | 30.5.1934
SUF2INV15 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV15 | TmpStk3_Pcb_F | ?C | 30.5.1935
SUF2INV15 | 106 | MV transformer pressure | SU F2 INV15 | PresTrf_F | "-" | 30.5.1936
SUF2INV15 | 110 | Switching status of the DC load-break switch | SU F2 INV15 | DcSwStt | "-" | 30.5.1937
SUINV15JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV15 | Dat_UpdCnt_1 | "-" | 30.5.1938
SUINV15JB1 | 2 | DC current input 1 | SU F2 INV15 | DcMs_Amp_01 | A | 30.5.1939
SUINV15JB1 | 3 | DC current input 2 | SU F2 INV15 | DcMs_Amp_02 | A | 30.5.1940
SUINV15JB1 | 4 | DC current input 3 | SU F2 INV15 | DcMs_Amp_03 | A | 30.5.1941
SUINV15JB1 | 5 | DC current input 4 | SU F2 INV15 | DcMs_Amp_04 | A | 30.5.1942
SUINV15JB1 | 6 | DC current input 5 | SU F2 INV15 | DcMs_Amp_05 | A | 30.5.1943
SUINV15JB1 | 7 | DC current input 6 | SU F2 INV15 | DcMs_Amp_06 | A | 30.5.1944
SUINV15JB1 | 8 | DC current input 7 | SU F2 INV15 | DcMs_Amp_07 | A | 30.5.1945
SUINV15JB1 | 9 | DC current input 8 | SU F2 INV15 | DcMs_Amp_08 | A | 30.5.1946
SUINV15JB1 | 10 | DC current input 9 | SU F2 INV15 | DcMs_Amp_09 | A | 30.5.1947
SUINV15JB1 | 11 | DC current input 10 | SU F2 INV15 | DcMs_Amp_10 | A | 30.5.1948
SUINV15JB1 | 12 | DC current input 11 | SU F2 INV15 | DcMs_Amp_11 | A | 30.5.1949
SUINV15JB1 | 13 | DC current input 12 | SU F2 INV15 | DcMs_Amp_12 | A | 30.5.1950
SUINV15JB1 | 14 | DC current input 13 | SU F2 INV15 | DcMs_Amp_13 | A | 30.5.1951
SUINV15JB1 | 15 | DC current input 14 | SU F2 INV15 | DcMs_Amp_14 | A | 30.5.1952
SUINV15JB1 | 16 | DC current input 15 | SU F2 INV15 | DcMs_Amp_15 | A | 30.5.1953
SUINV15JB1 | 17 | DC current input 16 | SU F2 INV15 | DcMs_Amp_16 | A | 30.5.1954
SUINV15JB1 | 18 | DC current input 1 | SU F2 INV15 | DcMs_Amp_01_F | A | 30.5.1955
SUINV15JB1 | 19 | DC current input 2 | SU F2 INV15 | DcMs_Amp_02_F | A | 30.5.1956
SUINV15JB1 | 20 | DC current input 3 | SU F2 INV15 | DcMs_Amp_03_F | A | 30.5.1957
SUINV15JB1 | 21 | DC current input 4 | SU F2 INV15 | DcMs_Amp_04_F | A | 30.5.1958
SUINV15JB1 | 22 | DC current input 5 | SU F2 INV15 | DcMs_Amp_05_F | A | 30.5.1959
SUINV15JB1 | 23 | DC current input 6 | SU F2 INV15 | DcMs_Amp_06_F | A | 30.5.1960
SUINV15JB1 | 24 | DC current input 7 | SU F2 INV15 | DcMs_Amp_07_F | A | 30.5.1961
SUINV15JB1 | 25 | DC current input 8 | SU F2 INV15 | DcMs_Amp_08_F | A | 30.5.1962
SUINV15JB1 | 26 | DC current input 9 | SU F2 INV15 | DcMs_Amp_09_F | A | 30.5.1963
SUINV15JB1 | 27 | DC current input 10 | SU F2 INV15 | DcMs_Amp_10_F | A | 30.5.1964
SUINV15JB1 | 28 | DC current input 11 | SU F2 INV15 | DcMs_Amp_11_F | A | 30.5.1965
SUINV15JB1 | 29 | DC current input 12 | SU F2 INV15 | DcMs_Amp_12_F | A | 30.5.1966
SUINV15JB1 | 30 | DC current input 13 | SU F2 INV15 | DcMs_Amp_13_F | A | 30.5.1967
SUINV15JB1 | 31 | DC current input 14 | SU F2 INV15 | DcMs_Amp_14_F | A | 30.5.1968
SUINV15JB1 | 32 | DC current input 15 | SU F2 INV15 | DcMs_Amp_15_F | A | 30.5.1969
SUINV15JB1 | 33 | DC current input 16 | SU F2 INV15 | DcMs_Amp_16_F | A | 30.5.1970
SUINV15JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV15 | Dat_UpdCnt_1 | "-" | 30.5.1971
SUINV15JB2 | 2 | DC current input 1 | SU F2 INV15 | DcMs_Amp_01 | A | 30.5.1972
SUINV15JB2 | 3 | DC current input 2 | SU F2 INV15 | DcMs_Amp_02 | A | 30.5.1973
SUINV15JB2 | 4 | DC current input 3 | SU F2 INV15 | DcMs_Amp_03 | A | 30.5.1974
SUINV15JB2 | 5 | DC current input 4 | SU F2 INV15 | DcMs_Amp_04 | A | 30.5.1975
SUINV15JB2 | 6 | DC current input 5 | SU F2 INV15 | DcMs_Amp_05 | A | 30.5.1976
SUINV15JB2 | 7 | DC current input 6 | SU F2 INV15 | DcMs_Amp_06 | A | 30.5.1977
SUINV15JB2 | 8 | DC current input 7 | SU F2 INV15 | DcMs_Amp_07 | A | 30.5.1978
SUINV15JB2 | 9 | DC current input 8 | SU F2 INV15 | DcMs_Amp_08 | A | 30.5.1979
SUINV15JB2 | 10 | DC current input 9 | SU F2 INV15 | DcMs_Amp_09 | A | 30.5.1980
SUINV15JB2 | 11 | DC current input 10 | SU F2 INV15 | DcMs_Amp_10 | A | 30.5.1981
SUINV15JB2 | 12 | DC current input 11 | SU F2 INV15 | DcMs_Amp_11 | A | 30.5.1982
SUINV15JB2 | 13 | DC current input 12 | SU F2 INV15 | DcMs_Amp_12 | A | 30.5.1983
SUINV15JB2 | 14 | DC current input 13 | SU F2 INV15 | DcMs_Amp_13 | A | 30.5.1984
SUINV15JB2 | 15 | DC current input 14 | SU F2 INV15 | DcMs_Amp_14 | A | 30.5.1985
SUINV15JB2 | 16 | DC current input 15 | SU F2 INV15 | DcMs_Amp_15 | A | 30.5.1986
SUINV15JB2 | 17 | DC current input 16 | SU F2 INV15 | DcMs_Amp_16 | A | 30.5.1987
SUINV15JB2 | 18 | DC current input 1 | SU F2 INV15 | DcMs_Amp_01_F | A | 30.5.1988
SUINV15JB2 | 19 | DC current input 2 | SU F2 INV15 | DcMs_Amp_02_F | A | 30.5.1989
SUINV15JB2 | 20 | DC current input 3 | SU F2 INV15 | DcMs_Amp_03_F | A | 30.5.1990
SUINV15JB2 | 21 | DC current input 4 | SU F2 INV15 | DcMs_Amp_04_F | A | 30.5.1991
SUINV15JB2 | 22 | DC current input 5 | SU F2 INV15 | DcMs_Amp_05_F | A | 30.5.1992
SUINV15JB2 | 23 | DC current input 6 | SU F2 INV15 | DcMs_Amp_06_F | A | 30.5.1993
SUINV15JB2 | 24 | DC current input 7 | SU F2 INV15 | DcMs_Amp_07_F | A | 30.5.1994
SUINV15JB2 | 25 | DC current input 8 | SU F2 INV15 | DcMs_Amp_08_F | A | 30.5.1995
SUINV15JB2 | 26 | DC current input 9 | SU F2 INV15 | DcMs_Amp_09_F | A | 30.5.1996
SUINV15JB2 | 27 | DC current input 10 | SU F2 INV15 | DcMs_Amp_10_F | A | 30.5.1997
SUINV15JB2 | 28 | DC current input 11 | SU F2 INV15 | DcMs_Amp_11_F | A | 30.5.1998
SUINV15JB2 | 29 | DC current input 12 | SU F2 INV15 | DcMs_Amp_12_F | A | 30.5.1999
SUINV15JB2 | 30 | DC current input 13 | SU F2 INV15 | DcMs_Amp_13_F | A | 30.5.2000
SUINV15JB2 | 31 | DC current input 14 | SU F2 INV15 | DcMs_Amp_14_F | A | 30.5.2001
SUINV15JB2 | 32 | DC current input 15 | SU F2 INV15 | DcMs_Amp_15_F | A | 30.5.2002
SUINV15JB2 | 33 | DC current input 16 | SU F2 INV15 | DcMs_Amp_16_F | A | 30.5.2003
SUF2INV16 | 1 | DC voltage DC plus to DC minus | SU F2 INV16 | DcMs_Vol | V | 30.5.2004
SUF2INV16 | 2 | DC current inverter bridge 1 | SU F2 INV16 | DcMs_Amp_Stk1 | A | 30.5.2005
SUF2INV16 | 3 | DC current inverter bridge 2 | SU F2 INV16 | DcMs_Amp_Stk2 | A | 30.5.2006
SUF2INV16 | 4 | DC current inverter bridge 3 | SU F2 INV16 | DcMs_Amp_Stk3 | A | 30.5.2007
SUF2INV16 | 5 | DC current, total | SU F2 INV16 | DcMs_TotAmp | A | 30.5.2008
SUF2INV16 | 6 | DC power, total | SU F2 INV16 | DcMs_TotWatt | kW | 30.5.2009
SUF2INV16 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV16 | InvMs_DclVol_Stk1 | V | 30.5.2010
SUF2INV16 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV16 | InvMs_DclVol_Stk2 | V | 30.5.2011
SUF2INV16 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV16 | InvMs_DclVol_Stk3 | V | 30.5.2012
SUF2INV16 | 10 | AC current L1, total | SU F2 INV16 | InvMs_TotA_PhsA | A | 30.5.2013
SUF2INV16 | 11 | AC current L2, total | SU F2 INV16 | InvMs_TotA_PhsB | A | 30.5.2014
SUF2INV16 | 12 | AC current L3, total | SU F2 INV16 | InvMs_TotA_PhsC | A | 30.5.2015
SUF2INV16 | 13 | Power factor (cos phi) | SU F2 INV16 | InvMs_PF | "-" | 30.5.2016
SUF2INV16 | 14 | Apparent power, total | SU F2 INV16 | InvMs_TotVA | kVA | 30.5.2017
SUF2INV16 | 15 | Active power, total | SU F2 INV16 | InvMs_TotW | kW | 30.5.2018
SUF2INV16 | 16 | Reactive power, total | SU F2 INV16 | InvMs_TotVAr | kVAr | 30.5.2019
SUF2INV16 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV16 | GriMs_V_PhsAB | V | 30.5.2020
SUF2INV16 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV16 | GriMs_V_PhsBC | V | 30.5.2021
SUF2INV16 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV16 | GriMs_V_PhsCA | V | 30.5.2022
SUF2INV16 | 20 | Power frequency | SU F2 INV16 | GriMs_Hz | Hz | 30.5.2023
SUF2INV16 | 21 | Temperature in the AC range | SU F2 INV16 | TmpCab_Acc | °C | 30.5.2024
SUF2INV16 | 22 | Temperature in the DC range | SU F2 INV16 | TmpCab_Dcc | °C | 30.5.2025
SUF2INV16 | 23 | Temperature in the electronics area | SU F2 INV16 | TmpCab_Rio | °C | 30.5.2026
SUF2INV16 | 24 | Temperature in interior, maximum value | SU F2 INV16 | TmpCab_Max | °C | 30.5.2027
SUF2INV16 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV16 | TmpStk_IgbtMax | °C | 30.5.2028
SUF2INV16 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV16 | TmpStk_PcbMax | °C | 30.5.2029
SUF2INV16 | 27 | Outside temperature | SU F2 INV16 | TmpExl | ?C | 30.5.2030
SUF2INV16 | 28 | Temperature of the MV transformer | SU F2 INV16 | TmpTrf | °C | 30.5.2031
SUF2INV16 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV16 | DcSw1Stt | "-" | 30.5.2032
SUF2INV16 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV16 | DcSw2Stt | "-" | 30.5.2033
SUF2INV16 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV16 | DcSw3Stt | "-" | 30.5.2034
SUF2INV16 | 32 | Switching status of the AC circuit breaker | SU F2 INV16 | AcSwStt | "-" | 30.5.2035
SUF2INV16 | 33 | Switching state of the capacitor contactor | SU F2 INV16 | CapacSwStt | "-" | 30.5.2036
SUF2INV16 | 34 | Switching status of the pre-charging contactor | SU F2 INV16 | PrchrgSwStt | "-" | 30.5.2037
SUF2INV16 | 35 | Feed-in hours | SU F2 INV16 | Cnt_TotFeedTm | "-" | 30.5.2038
SUF2INV16 | 36 | Operating hours | SU F2 INV16 | Cnt_TotOpTm | "-" | 30.5.2039
SUF2INV16 | 37 | DC energy drawn, total | SU F2 INV16 | Cnt_TotWatthIn | MWh | 30.5.2040
SUF2INV16 | 38 | AC energy fed in, total | SU F2 INV16 | Cnt_TotWhOut | MWh | 30.5.2041
SUF2INV16 | 39 | DC energy drawn that day | SU F2 INV16 | Cnt_WatthIn | MWh | 30.5.2042
SUF2INV16 | 40 | AC energy fed in that day | SU F2 INV16 | Cnt_WhOut | MWh | 30.5.2043
SUF2INV16 | 41 | Operating hours of the interior fan 1 | SU F2 INV16 | Cnt_FanCab1Tm | "-" | 30.5.2044
SUF2INV16 | 42 | Operating hours of the interior fan 2 | SU F2 INV16 | Cnt_FanCab2Tm | "-" | 30.5.2045
SUF2INV16 | 43 | Operating hours of the inverter bridge fan | SU F2 INV16 | Cnt_FanStkTm | "-" | 30.5.2046
SUF2INV16 | 44 | Operating hours of the internal heating element | SU F2 INV16 | Cnt_HtCabTm | "-" | 30.5.2047
SUF2INV16 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV16 | Cnt_HtLoExlTmpTm | "-" | 30.5.2048
SUF2INV16 | 46 | Error location of the present error | SU F2 INV16 | ErrLcn | "-" | 30.5.2049
SUF2INV16 | 47 | Error status of the inverter | SU F2 INV16 | ErrStt | "-" | 30.5.2050
SUF2INV16 | 48 | Error number of the present error | SU F2 INV16 | ErrNo | "-" | 30.5.2051
SUF2INV16 | 49 | Operating state of the inverter | SU F2 INV16 | OpStt | "-" | 30.5.2052
SUF2INV16 | 50 | Switch status of the start-stop key switch | SU F2 INV16 | Rio_KeySw | "-" | 30.5.2053
SUF2INV16 | 51 | Waiting time for grid connection | SU F2 INV16 | WaitGriTm | s | 30.5.2054
SUF2INV16 | 52 | Inverter serial number | SU F2 INV16 | DevInf_SerNo | "-" | 30.5.2055
SUF2INV16 | 53 | Switching status of the GFDI | SU F2 INV16 | GfdiSwStt | "-" | 30.5.2056
SUF2INV16 | 54 | Active power, setpoint | SU F2 INV16 | WSpt | kW | 30.5.2057
SUF2INV16 | 55 | Maximum apparent power, setpoint | SU F2 INV16 | VAMaxSpt | kVA | 30.5.2058
SUF2INV16 | 56 | Reactive power, setpoint | SU F2 INV16 | VArSpt | kVAr | 30.5.2059
SUF2INV16 | 57 | Power factor cos (phi), setpoint | SU F2 INV16 | PFSpt | "-" | 30.5.2060
SUF2INV16 | 58 | Fast stop hermetic protection, pressure | SU F2 INV16 | TrfPro_Pres | "-" | 30.5.2061
SUF2INV16 | 59 | Fast stop hermetic protection, temperature | SU F2 INV16 | TrfPro_TmpTrp | "-" | 30.5.2062
SUF2INV16 | 60 | Hermetic protection, gas fill level | SU F2 INV16 | TrfPro_GasOilLev | "-" | 30.5.2063
SUF2INV16 | 61 | Hermetic pressure, temperature warning | SU F2 INV16 | TrfPro_TmpWrn | "-" | 30.5.2064
SUF2INV16 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV16 | TmpStk1_Igbt | °C | 30.5.2065
SUF2INV16 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV16 | TmpStk2_Igbt | °C | 30.5.2066
SUF2INV16 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV16 | TmpStk3_Igbt | °C | 30.5.2067
SUF2INV16 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV16 | TmpStk1_Pcb | ?C | 30.5.2068
SUF2INV16 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV16 | TmpStk2_Pcb | ?C | 30.5.2069
SUF2INV16 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV16 | TmpStk3_Pcb | ?C | 30.5.2070
SUF2INV16 | 68 | AC Energy Fed in the previous Day | SU F2 INV16 | Cnt_YstdWhOut | MWh | 30.5.2071
SUF2INV16 | 69 | CPU running time since system start | SU F2 INV16 | Cpu1UpTime | s | 30.5.2072
SUF2INV16 | 70 | Insulation resistance | SU F2 INV16 | PvGnd_RisIso | kOhm | 30.5.2073
SUF2INV16 | 71 | MV transformer pressure | SU F2 INV16 | PresTrf | "-" | 30.5.2074
SUF2INV16 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV16 | PresTrf_ErrStt | "-" | 30.5.2075
SUF2INV16 | 73 | DC voltage DC plus to DC minus | SU F2 INV16 | DcMs_Vol_F | V | 30.5.2076
SUF2INV16 | 74 | DC current inverter bridge 1 | SU F2 INV16 | DcMs_Amp_Stk1_F | A | 30.5.2077
SUF2INV16 | 75 | DC current inverter bridge 2 | SU F2 INV16 | DcMs_Amp_Stk2_F | A | 30.5.2078
SUF2INV16 | 76 | DC current inverter bridge 3 | SU F2 INV16 | DcMs_Amp_Stk3_F | A | 30.5.2079
SUF2INV16 | 77 | DC current, total | SU F2 INV16 | DcMs_TotAmp_F | A | 30.5.2080
SUF2INV16 | 78 | DC power, total | SU F2 INV16 | DcMs_TotWatt_F | kW | 30.5.2081
SUF2INV16 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV16 | InvMs_DclVol_Stk1_F | V | 30.5.2082
SUF2INV16 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV16 | InvMs_DclVol_Stk2_F | V | 30.5.2083
SUF2INV16 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV16 | InvMs_DclVol_Stk3_F | V | 30.5.2084
SUF2INV16 | 82 | AC current L1, total | SU F2 INV16 | InvMs_TotA_PhsA_F | A | 30.5.2085
SUF2INV16 | 83 | AC current L2, total | SU F2 INV16 | InvMs_TotA_PhsB_F | A | 30.5.2086
SUF2INV16 | 84 | AC current L3, total | SU F2 INV16 | InvMs_TotA_PhsC_F | A | 30.5.2087
SUF2INV16 | 85 | Power factor (cos phi) | SU F2 INV16 | InvMs_PF_F | "-" | 30.5.2088
SUF2INV16 | 86 | Active power, total | SU F2 INV16 | InvMs_TotW_F | kW | 30.5.2089
SUF2INV16 | 87 | Reactive power, total | SU F2 INV16 | InvMs_TotVAr_F | kVAr | 30.5.2090
SUF2INV16 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV16 | GriMs_V_PhsAB_F | V | 30.5.2091
SUF2INV16 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV16 | GriMs_V_PhsBC_F | V | 30.5.2092
SUF2INV16 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV16 | GriMs_V_PhsCA_F | V | 30.5.2093
SUF2INV16 | 91 | Power frequency | SU F2 INV16 | GriMs_Hz_F | Hz | 30.5.2094
SUF2INV16 | 92 | Temperature in the AC range | SU F2 INV16 | TmpCab_Acc_F | °C | 30.5.2095
SUF2INV16 | 93 | Temperature in the DC range | SU F2 INV16 | TmpCab_Dcc_F | °C | 30.5.2096
SUF2INV16 | 94 | Temperature in the electronics area | SU F2 INV16 | TmpCab_Rio_F | °C | 30.5.2097
SUF2INV16 | 95 | Temperature in interior, maximum value | SU F2 INV16 | TmpCab_Max_F | °C | 30.5.2098
SUF2INV16 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV16 | TmpStk_IgbtMax_F | °C | 30.5.2099
SUF2INV16 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV16 | TmpStk_PcbMax_F | °C | 30.5.2100
SUF2INV16 | 98 | Outside temperature | SU F2 INV16 | TmpExl_F | ?C | 30.5.2101
SUF2INV16 | 99 | Temperature of the MV transformer | SU F2 INV16 | TmpTrf_F | °C | 30.5.2102
SUF2INV16 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV16 | TmpStk1_Igbt_F | °C | 30.5.2103
SUF2INV16 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV16 | TmpStk2_Igbt_F | °C | 30.5.2104
SUF2INV16 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV16 | TmpStk3_Igbt_F | °C | 30.5.2105
SUF2INV16 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV16 | TmpStk1_Pcb_F | ?C | 30.5.2106
SUF2INV16 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV16 | TmpStk2_Pcb_F | ?C | 30.5.2107
SUF2INV16 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV16 | TmpStk3_Pcb_F | ?C | 30.5.2108
SUF2INV16 | 106 | MV transformer pressure | SU F2 INV16 | PresTrf_F | "-" | 30.5.2109
SUF2INV16 | 110 | Switching status of the DC load-break switch | SU F2 INV16 | DcSwStt | "-" | 30.5.2110
SUINV16JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV16 | Dat_UpdCnt_1 | "-" | 30.5.2111
SUINV16JB1 | 2 | DC current input 1 | SU F2 INV16 | DcMs_Amp_01 | A | 30.5.2112
SUINV16JB1 | 3 | DC current input 2 | SU F2 INV16 | DcMs_Amp_02 | A | 30.5.2113
SUINV16JB1 | 4 | DC current input 3 | SU F2 INV16 | DcMs_Amp_03 | A | 30.5.2114
SUINV16JB1 | 5 | DC current input 4 | SU F2 INV16 | DcMs_Amp_04 | A | 30.5.2115
SUINV16JB1 | 6 | DC current input 5 | SU F2 INV16 | DcMs_Amp_05 | A | 30.5.2116
SUINV16JB1 | 7 | DC current input 6 | SU F2 INV16 | DcMs_Amp_06 | A | 30.5.2117
SUINV16JB1 | 8 | DC current input 7 | SU F2 INV16 | DcMs_Amp_07 | A | 30.5.2118
SUINV16JB1 | 9 | DC current input 8 | SU F2 INV16 | DcMs_Amp_08 | A | 30.5.2119
SUINV16JB1 | 10 | DC current input 9 | SU F2 INV16 | DcMs_Amp_09 | A | 30.5.2120
SUINV16JB1 | 11 | DC current input 10 | SU F2 INV16 | DcMs_Amp_10 | A | 30.5.2121
SUINV16JB1 | 12 | DC current input 11 | SU F2 INV16 | DcMs_Amp_11 | A | 30.5.2122
SUINV16JB1 | 13 | DC current input 12 | SU F2 INV16 | DcMs_Amp_12 | A | 30.5.2123
SUINV16JB1 | 14 | DC current input 13 | SU F2 INV16 | DcMs_Amp_13 | A | 30.5.2124
SUINV16JB1 | 15 | DC current input 14 | SU F2 INV16 | DcMs_Amp_14 | A | 30.5.2125
SUINV16JB1 | 16 | DC current input 15 | SU F2 INV16 | DcMs_Amp_15 | A | 30.5.2126
SUINV16JB1 | 17 | DC current input 16 | SU F2 INV16 | DcMs_Amp_16 | A | 30.5.2127
SUINV16JB1 | 18 | DC current input 1 | SU F2 INV16 | DcMs_Amp_01_F | A | 30.5.2128
SUINV16JB1 | 19 | DC current input 2 | SU F2 INV16 | DcMs_Amp_02_F | A | 30.5.2129
SUINV16JB1 | 20 | DC current input 3 | SU F2 INV16 | DcMs_Amp_03_F | A | 30.5.2130
SUINV16JB1 | 21 | DC current input 4 | SU F2 INV16 | DcMs_Amp_04_F | A | 30.5.2131
SUINV16JB1 | 22 | DC current input 5 | SU F2 INV16 | DcMs_Amp_05_F | A | 30.5.2132
SUINV16JB1 | 23 | DC current input 6 | SU F2 INV16 | DcMs_Amp_06_F | A | 30.5.2133
SUINV16JB1 | 24 | DC current input 7 | SU F2 INV16 | DcMs_Amp_07_F | A | 30.5.2134
SUINV16JB1 | 25 | DC current input 8 | SU F2 INV16 | DcMs_Amp_08_F | A | 30.5.2135
SUINV16JB1 | 26 | DC current input 9 | SU F2 INV16 | DcMs_Amp_09_F | A | 30.5.2136
SUINV16JB1 | 27 | DC current input 10 | SU F2 INV16 | DcMs_Amp_10_F | A | 30.5.2137
SUINV16JB1 | 28 | DC current input 11 | SU F2 INV16 | DcMs_Amp_11_F | A | 30.5.2138
SUINV16JB1 | 29 | DC current input 12 | SU F2 INV16 | DcMs_Amp_12_F | A | 30.5.2139
SUINV16JB1 | 30 | DC current input 13 | SU F2 INV16 | DcMs_Amp_13_F | A | 30.5.2140
SUINV16JB1 | 31 | DC current input 14 | SU F2 INV16 | DcMs_Amp_14_F | A | 30.5.2141
SUINV16JB1 | 32 | DC current input 15 | SU F2 INV16 | DcMs_Amp_15_F | A | 30.5.2142
SUINV16JB1 | 33 | DC current input 16 | SU F2 INV16 | DcMs_Amp_16_F | A | 30.5.2143
SUINV16JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV16 | Dat_UpdCnt_1 | "-" | 30.5.2144
SUINV16JB2 | 2 | DC current input 1 | SU F2 INV16 | DcMs_Amp_01 | A | 30.5.2145
SUINV16JB2 | 3 | DC current input 2 | SU F2 INV16 | DcMs_Amp_02 | A | 30.5.2146
SUINV16JB2 | 4 | DC current input 3 | SU F2 INV16 | DcMs_Amp_03 | A | 30.5.2147
SUINV16JB2 | 5 | DC current input 4 | SU F2 INV16 | DcMs_Amp_04 | A | 30.5.2148
SUINV16JB2 | 6 | DC current input 5 | SU F2 INV16 | DcMs_Amp_05 | A | 30.5.2149
SUINV16JB2 | 7 | DC current input 6 | SU F2 INV16 | DcMs_Amp_06 | A | 30.5.2150
SUINV16JB2 | 8 | DC current input 7 | SU F2 INV16 | DcMs_Amp_07 | A | 30.5.2151
SUINV16JB2 | 9 | DC current input 8 | SU F2 INV16 | DcMs_Amp_08 | A | 30.5.2152
SUINV16JB2 | 10 | DC current input 9 | SU F2 INV16 | DcMs_Amp_09 | A | 30.5.2153
SUINV16JB2 | 11 | DC current input 10 | SU F2 INV16 | DcMs_Amp_10 | A | 30.5.2154
SUINV16JB2 | 12 | DC current input 11 | SU F2 INV16 | DcMs_Amp_11 | A | 30.5.2155
SUINV16JB2 | 13 | DC current input 12 | SU F2 INV16 | DcMs_Amp_12 | A | 30.5.2156
SUINV16JB2 | 14 | DC current input 13 | SU F2 INV16 | DcMs_Amp_13 | A | 30.5.2157
SUINV16JB2 | 15 | DC current input 14 | SU F2 INV16 | DcMs_Amp_14 | A | 30.5.2158
SUINV16JB2 | 16 | DC current input 15 | SU F2 INV16 | DcMs_Amp_15 | A | 30.5.2159
SUINV16JB2 | 17 | DC current input 16 | SU F2 INV16 | DcMs_Amp_16 | A | 30.5.2160
SUINV16JB2 | 18 | DC current input 1 | SU F2 INV16 | DcMs_Amp_01_F | A | 30.5.2161
SUINV16JB2 | 19 | DC current input 2 | SU F2 INV16 | DcMs_Amp_02_F | A | 30.5.2162
SUINV16JB2 | 20 | DC current input 3 | SU F2 INV16 | DcMs_Amp_03_F | A | 30.5.2163
SUINV16JB2 | 21 | DC current input 4 | SU F2 INV16 | DcMs_Amp_04_F | A | 30.5.2164
SUINV16JB2 | 22 | DC current input 5 | SU F2 INV16 | DcMs_Amp_05_F | A | 30.5.2165
SUINV16JB2 | 23 | DC current input 6 | SU F2 INV16 | DcMs_Amp_06_F | A | 30.5.2166
SUINV16JB2 | 24 | DC current input 7 | SU F2 INV16 | DcMs_Amp_07_F | A | 30.5.2167
SUINV16JB2 | 25 | DC current input 8 | SU F2 INV16 | DcMs_Amp_08_F | A | 30.5.2168
SUINV16JB2 | 26 | DC current input 9 | SU F2 INV16 | DcMs_Amp_09_F | A | 30.5.2169
SUINV16JB2 | 27 | DC current input 10 | SU F2 INV16 | DcMs_Amp_10_F | A | 30.5.2170
SUINV16JB2 | 28 | DC current input 11 | SU F2 INV16 | DcMs_Amp_11_F | A | 30.5.2171
SUINV16JB2 | 29 | DC current input 12 | SU F2 INV16 | DcMs_Amp_12_F | A | 30.5.2172
SUINV16JB2 | 30 | DC current input 13 | SU F2 INV16 | DcMs_Amp_13_F | A | 30.5.2173
SUINV16JB2 | 31 | DC current input 14 | SU F2 INV16 | DcMs_Amp_14_F | A | 30.5.2174
SUINV16JB2 | 32 | DC current input 15 | SU F2 INV16 | DcMs_Amp_15_F | A | 30.5.2175
SUINV16JB2 | 33 | DC current input 16 | SU F2 INV16 | DcMs_Amp_16_F | A | 30.5.2176
SUF2INV19 | 1 | DC voltage DC plus to DC minus | SU F2 INV19 | DcMs_Vol | V | 30.5.2177
SUF2INV19 | 2 | DC current inverter bridge 1 | SU F2 INV19 | DcMs_Amp_Stk1 | A | 30.5.2178
SUF2INV19 | 3 | DC current inverter bridge 2 | SU F2 INV19 | DcMs_Amp_Stk2 | A | 30.5.2179
SUF2INV19 | 4 | DC current inverter bridge 3 | SU F2 INV19 | DcMs_Amp_Stk3 | A | 30.5.2180
SUF2INV19 | 5 | DC current, total | SU F2 INV19 | DcMs_TotAmp | A | 30.5.2181
SUF2INV19 | 6 | DC power, total | SU F2 INV19 | DcMs_TotWatt | kW | 30.5.2182
SUF2INV19 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV19 | InvMs_DclVol_Stk1 | V | 30.5.2183
SUF2INV19 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV19 | InvMs_DclVol_Stk2 | V | 30.5.2184
SUF2INV19 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV19 | InvMs_DclVol_Stk3 | V | 30.5.2185
SUF2INV19 | 10 | AC current L1, total | SU F2 INV19 | InvMs_TotA_PhsA | A | 30.5.2186
SUF2INV19 | 11 | AC current L2, total | SU F2 INV19 | InvMs_TotA_PhsB | A | 30.5.2187
SUF2INV19 | 12 | AC current L3, total | SU F2 INV19 | InvMs_TotA_PhsC | A | 30.5.2188
SUF2INV19 | 13 | Power factor (cos phi) | SU F2 INV19 | InvMs_PF | "-" | 30.5.2189
SUF2INV19 | 14 | Apparent power, total | SU F2 INV19 | InvMs_TotVA | kVA | 30.5.2190
SUF2INV19 | 15 | Active power, total | SU F2 INV19 | InvMs_TotW | kW | 30.5.2191
SUF2INV19 | 16 | Reactive power, total | SU F2 INV19 | InvMs_TotVAr | kVAr | 30.5.2192
SUF2INV19 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV19 | GriMs_V_PhsAB | V | 30.5.2193
SUF2INV19 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV19 | GriMs_V_PhsBC | V | 30.5.2194
SUF2INV19 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV19 | GriMs_V_PhsCA | V | 30.5.2195
SUF2INV19 | 20 | Power frequency | SU F2 INV19 | GriMs_Hz | Hz | 30.5.2196
SUF2INV19 | 21 | Temperature in the AC range | SU F2 INV19 | TmpCab_Acc | °C | 30.5.2197
SUF2INV19 | 22 | Temperature in the DC range | SU F2 INV19 | TmpCab_Dcc | °C | 30.5.2198
SUF2INV19 | 23 | Temperature in the electronics area | SU F2 INV19 | TmpCab_Rio | °C | 30.5.2199
SUF2INV19 | 24 | Temperature in interior, maximum value | SU F2 INV19 | TmpCab_Max | °C | 30.5.2200
SUF2INV19 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV19 | TmpStk_IgbtMax | °C | 30.5.2201
SUF2INV19 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV19 | TmpStk_PcbMax | °C | 30.5.2202
SUF2INV19 | 27 | Outside temperature | SU F2 INV19 | TmpExl | ?C | 30.5.2203
SUF2INV19 | 28 | Temperature of the MV transformer | SU F2 INV19 | TmpTrf | °C | 30.5.2204
SUF2INV19 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV19 | DcSw1Stt | "-" | 30.5.2205
SUF2INV19 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV19 | DcSw2Stt | "-" | 30.5.2206
SUF2INV19 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV19 | DcSw3Stt | "-" | 30.5.2207
SUF2INV19 | 32 | Switching status of the AC circuit breaker | SU F2 INV19 | AcSwStt | "-" | 30.5.2208
SUF2INV19 | 33 | Switching state of the capacitor contactor | SU F2 INV19 | CapacSwStt | "-" | 30.5.2209
SUF2INV19 | 34 | Switching status of the pre-charging contactor | SU F2 INV19 | PrchrgSwStt | "-" | 30.5.2210
SUF2INV19 | 35 | Feed-in hours | SU F2 INV19 | Cnt_TotFeedTm | "-" | 30.5.2211
SUF2INV19 | 36 | Operating hours | SU F2 INV19 | Cnt_TotOpTm | "-" | 30.5.2212
SUF2INV19 | 37 | DC energy drawn, total | SU F2 INV19 | Cnt_TotWatthIn | MWh | 30.5.2213
SUF2INV19 | 38 | AC energy fed in, total | SU F2 INV19 | Cnt_TotWhOut | MWh | 30.5.2214
SUF2INV19 | 39 | DC energy drawn that day | SU F2 INV19 | Cnt_WatthIn | MWh | 30.5.2215
SUF2INV19 | 40 | AC energy fed in that day | SU F2 INV19 | Cnt_WhOut | MWh | 30.5.2216
SUF2INV19 | 41 | Operating hours of the interior fan 1 | SU F2 INV19 | Cnt_FanCab1Tm | "-" | 30.5.2217
SUF2INV19 | 42 | Operating hours of the interior fan 2 | SU F2 INV19 | Cnt_FanCab2Tm | "-" | 30.5.2218
SUF2INV19 | 43 | Operating hours of the inverter bridge fan | SU F2 INV19 | Cnt_FanStkTm | "-" | 30.5.2219
SUF2INV19 | 44 | Operating hours of the internal heating element | SU F2 INV19 | Cnt_HtCabTm | "-" | 30.5.2220
SUF2INV19 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV19 | Cnt_HtLoExlTmpTm | "-" | 30.5.2221
SUF2INV19 | 46 | Error location of the present error | SU F2 INV19 | ErrLcn | "-" | 30.5.2222
SUF2INV19 | 47 | Error status of the inverter | SU F2 INV19 | ErrStt | "-" | 30.5.2223
SUF2INV19 | 48 | Error number of the present error | SU F2 INV19 | ErrNo | "-" | 30.5.2224
SUF2INV19 | 49 | Operating state of the inverter | SU F2 INV19 | OpStt | "-" | 30.5.2225
SUF2INV19 | 50 | Switch status of the start-stop key switch | SU F2 INV19 | Rio_KeySw | "-" | 30.5.2226
SUF2INV19 | 51 | Waiting time for grid connection | SU F2 INV19 | WaitGriTm | s | 30.5.2227
SUF2INV19 | 52 | Inverter serial number | SU F2 INV19 | DevInf_SerNo | "-" | 30.5.2228
SUF2INV19 | 53 | Switching status of the GFDI | SU F2 INV19 | GfdiSwStt | "-" | 30.5.2229
SUF2INV19 | 54 | Active power, setpoint | SU F2 INV19 | WSpt | kW | 30.5.2230
SUF2INV19 | 55 | Maximum apparent power, setpoint | SU F2 INV19 | VAMaxSpt | kVA | 30.5.2231
SUF2INV19 | 56 | Reactive power, setpoint | SU F2 INV19 | VArSpt | kVAr | 30.5.2232
SUF2INV19 | 57 | Power factor cos (phi), setpoint | SU F2 INV19 | PFSpt | "-" | 30.5.2233
SUF2INV19 | 58 | Fast stop hermetic protection, pressure | SU F2 INV19 | TrfPro_Pres | "-" | 30.5.2234
SUF2INV19 | 59 | Fast stop hermetic protection, temperature | SU F2 INV19 | TrfPro_TmpTrp | "-" | 30.5.2235
SUF2INV19 | 60 | Hermetic protection, gas fill level | SU F2 INV19 | TrfPro_GasOilLev | "-" | 30.5.2236
SUF2INV19 | 61 | Hermetic pressure, temperature warning | SU F2 INV19 | TrfPro_TmpWrn | "-" | 30.5.2237
SUF2INV19 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV19 | TmpStk1_Igbt | °C | 30.5.2238
SUF2INV19 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV19 | TmpStk2_Igbt | °C | 30.5.2239
SUF2INV19 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV19 | TmpStk3_Igbt | °C | 30.5.2240
SUF2INV19 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV19 | TmpStk1_Pcb | ?C | 30.5.2241
SUF2INV19 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV19 | TmpStk2_Pcb | ?C | 30.5.2242
SUF2INV19 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV19 | TmpStk3_Pcb | ?C | 30.5.2243
SUF2INV19 | 68 | AC Energy Fed in the previous Day | SU F2 INV19 | Cnt_YstdWhOut | MWh | 30.5.2244
SUF2INV19 | 69 | CPU running time since system start | SU F2 INV19 | Cpu1UpTime | s | 30.5.2245
SUF2INV19 | 70 | Insulation resistance | SU F2 INV19 | PvGnd_RisIso | kOhm | 30.5.2246
SUF2INV19 | 71 | MV transformer pressure | SU F2 INV19 | PresTrf | "-" | 30.5.2247
SUF2INV19 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV19 | PresTrf_ErrStt | "-" | 30.5.2248
SUF2INV19 | 73 | DC voltage DC plus to DC minus | SU F2 INV19 | DcMs_Vol_F | V | 30.5.2249
SUF2INV19 | 74 | DC current inverter bridge 1 | SU F2 INV19 | DcMs_Amp_Stk1_F | A | 30.5.2250
SUF2INV19 | 75 | DC current inverter bridge 2 | SU F2 INV19 | DcMs_Amp_Stk2_F | A | 30.5.2251
SUF2INV19 | 76 | DC current inverter bridge 3 | SU F2 INV19 | DcMs_Amp_Stk3_F | A | 30.5.2252
SUF2INV19 | 77 | DC current, total | SU F2 INV19 | DcMs_TotAmp_F | A | 30.5.2253
SUF2INV19 | 78 | DC power, total | SU F2 INV19 | DcMs_TotWatt_F | kW | 30.5.2254
SUF2INV19 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV19 | InvMs_DclVol_Stk1_F | V | 30.5.2255
SUF2INV19 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV19 | InvMs_DclVol_Stk2_F | V | 30.5.2256
SUF2INV19 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV19 | InvMs_DclVol_Stk3_F | V | 30.5.2257
SUF2INV19 | 82 | AC current L1, total | SU F2 INV19 | InvMs_TotA_PhsA_F | A | 30.5.2258
SUF2INV19 | 83 | AC current L2, total | SU F2 INV19 | InvMs_TotA_PhsB_F | A | 30.5.2259
SUF2INV19 | 84 | AC current L3, total | SU F2 INV19 | InvMs_TotA_PhsC_F | A | 30.5.2260
SUF2INV19 | 85 | Power factor (cos phi) | SU F2 INV19 | InvMs_PF_F | "-" | 30.5.2261
SUF2INV19 | 86 | Active power, total | SU F2 INV19 | InvMs_TotW_F | kW | 30.5.2262
SUF2INV19 | 87 | Reactive power, total | SU F2 INV19 | InvMs_TotVAr_F | kVAr | 30.5.2263
SUF2INV19 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV19 | GriMs_V_PhsAB_F | V | 30.5.2264
SUF2INV19 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV19 | GriMs_V_PhsBC_F | V | 30.5.2265
SUF2INV19 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV19 | GriMs_V_PhsCA_F | V | 30.5.2266
SUF2INV19 | 91 | Power frequency | SU F2 INV19 | GriMs_Hz_F | Hz | 30.5.2267
SUF2INV19 | 92 | Temperature in the AC range | SU F2 INV19 | TmpCab_Acc_F | °C | 30.5.2268
SUF2INV19 | 93 | Temperature in the DC range | SU F2 INV19 | TmpCab_Dcc_F | °C | 30.5.2269
SUF2INV19 | 94 | Temperature in the electronics area | SU F2 INV19 | TmpCab_Rio_F | °C | 30.5.2270
SUF2INV19 | 95 | Temperature in interior, maximum value | SU F2 INV19 | TmpCab_Max_F | °C | 30.5.2271
SUF2INV19 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV19 | TmpStk_IgbtMax_F | °C | 30.5.2272
SUF2INV19 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV19 | TmpStk_PcbMax_F | °C | 30.5.2273
SUF2INV19 | 98 | Outside temperature | SU F2 INV19 | TmpExl_F | ?C | 30.5.2274
SUF2INV19 | 99 | Temperature of the MV transformer | SU F2 INV19 | TmpTrf_F | °C | 30.5.2275
SUF2INV19 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV19 | TmpStk1_Igbt_F | °C | 30.5.2276
SUF2INV19 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV19 | TmpStk2_Igbt_F | °C | 30.5.2277
SUF2INV19 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV19 | TmpStk3_Igbt_F | °C | 30.5.2278
SUF2INV19 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV19 | TmpStk1_Pcb_F | ?C | 30.5.2279
SUF2INV19 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV19 | TmpStk2_Pcb_F | ?C | 30.5.2280
SUF2INV19 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV19 | TmpStk3_Pcb_F | ?C | 30.5.2281
SUF2INV19 | 106 | MV transformer pressure | SU F2 INV19 | PresTrf_F | "-" | 30.5.2282
SUF2INV19 | 110 | Switching status of the DC load-break switch | SU F2 INV19 | DcSwStt | "-" | 30.5.2283
SUINV19JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV19 | Dat_UpdCnt_1 | "-" | 30.5.2284
SUINV19JB1 | 2 | DC current input 1 | SU F2 INV19 | DcMs_Amp_01 | A | 30.5.2285
SUINV19JB1 | 3 | DC current input 2 | SU F2 INV19 | DcMs_Amp_02 | A | 30.5.2286
SUINV19JB1 | 4 | DC current input 3 | SU F2 INV19 | DcMs_Amp_03 | A | 30.5.2287
SUINV19JB1 | 5 | DC current input 4 | SU F2 INV19 | DcMs_Amp_04 | A | 30.5.2288
SUINV19JB1 | 6 | DC current input 5 | SU F2 INV19 | DcMs_Amp_05 | A | 30.5.2289
SUINV19JB1 | 7 | DC current input 6 | SU F2 INV19 | DcMs_Amp_06 | A | 30.5.2290
SUINV19JB1 | 8 | DC current input 7 | SU F2 INV19 | DcMs_Amp_07 | A | 30.5.2291
SUINV19JB1 | 9 | DC current input 8 | SU F2 INV19 | DcMs_Amp_08 | A | 30.5.2292
SUINV19JB1 | 10 | DC current input 9 | SU F2 INV19 | DcMs_Amp_09 | A | 30.5.2293
SUINV19JB1 | 11 | DC current input 10 | SU F2 INV19 | DcMs_Amp_10 | A | 30.5.2294
SUINV19JB1 | 12 | DC current input 11 | SU F2 INV19 | DcMs_Amp_11 | A | 30.5.2295
SUINV19JB1 | 13 | DC current input 12 | SU F2 INV19 | DcMs_Amp_12 | A | 30.5.2296
SUINV19JB1 | 14 | DC current input 13 | SU F2 INV19 | DcMs_Amp_13 | A | 30.5.2297
SUINV19JB1 | 15 | DC current input 14 | SU F2 INV19 | DcMs_Amp_14 | A | 30.5.2298
SUINV19JB1 | 16 | DC current input 15 | SU F2 INV19 | DcMs_Amp_15 | A | 30.5.2299
SUINV19JB1 | 17 | DC current input 16 | SU F2 INV19 | DcMs_Amp_16 | A | 30.5.2300
SUINV19JB1 | 18 | DC current input 1 | SU F2 INV19 | DcMs_Amp_01_F | A | 30.5.2301
SUINV19JB1 | 19 | DC current input 2 | SU F2 INV19 | DcMs_Amp_02_F | A | 30.5.2302
SUINV19JB1 | 20 | DC current input 3 | SU F2 INV19 | DcMs_Amp_03_F | A | 30.5.2303
SUINV19JB1 | 21 | DC current input 4 | SU F2 INV19 | DcMs_Amp_04_F | A | 30.5.2304
SUINV19JB1 | 22 | DC current input 5 | SU F2 INV19 | DcMs_Amp_05_F | A | 30.5.2305
SUINV19JB1 | 23 | DC current input 6 | SU F2 INV19 | DcMs_Amp_06_F | A | 30.5.2306
SUINV19JB1 | 24 | DC current input 7 | SU F2 INV19 | DcMs_Amp_07_F | A | 30.5.2307
SUINV19JB1 | 25 | DC current input 8 | SU F2 INV19 | DcMs_Amp_08_F | A | 30.5.2308
SUINV19JB1 | 26 | DC current input 9 | SU F2 INV19 | DcMs_Amp_09_F | A | 30.5.2309
SUINV19JB1 | 27 | DC current input 10 | SU F2 INV19 | DcMs_Amp_10_F | A | 30.5.2310
SUINV19JB1 | 28 | DC current input 11 | SU F2 INV19 | DcMs_Amp_11_F | A | 30.5.2311
SUINV19JB1 | 29 | DC current input 12 | SU F2 INV19 | DcMs_Amp_12_F | A | 30.5.2312
SUINV19JB1 | 30 | DC current input 13 | SU F2 INV19 | DcMs_Amp_13_F | A | 30.5.2313
SUINV19JB1 | 31 | DC current input 14 | SU F2 INV19 | DcMs_Amp_14_F | A | 30.5.2314
SUINV19JB1 | 32 | DC current input 15 | SU F2 INV19 | DcMs_Amp_15_F | A | 30.5.2315
SUINV19JB1 | 33 | DC current input 16 | SU F2 INV19 | DcMs_Amp_16_F | A | 30.5.2316
SUINV19JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV19 | Dat_UpdCnt_1 | "-" | 30.5.2317
SUINV19JB2 | 2 | DC current input 1 | SU F2 INV19 | DcMs_Amp_01 | A | 30.5.2318
SUINV19JB2 | 3 | DC current input 2 | SU F2 INV19 | DcMs_Amp_02 | A | 30.5.2319
SUINV19JB2 | 4 | DC current input 3 | SU F2 INV19 | DcMs_Amp_03 | A | 30.5.2320
SUINV19JB2 | 5 | DC current input 4 | SU F2 INV19 | DcMs_Amp_04 | A | 30.5.2321
SUINV19JB2 | 6 | DC current input 5 | SU F2 INV19 | DcMs_Amp_05 | A | 30.5.2322
SUINV19JB2 | 7 | DC current input 6 | SU F2 INV19 | DcMs_Amp_06 | A | 30.5.2323
SUINV19JB2 | 8 | DC current input 7 | SU F2 INV19 | DcMs_Amp_07 | A | 30.5.2324
SUINV19JB2 | 9 | DC current input 8 | SU F2 INV19 | DcMs_Amp_08 | A | 30.5.2325
SUINV19JB2 | 10 | DC current input 9 | SU F2 INV19 | DcMs_Amp_09 | A | 30.5.2326
SUINV19JB2 | 11 | DC current input 10 | SU F2 INV19 | DcMs_Amp_10 | A | 30.5.2327
SUINV19JB2 | 12 | DC current input 11 | SU F2 INV19 | DcMs_Amp_11 | A | 30.5.2328
SUINV19JB2 | 13 | DC current input 12 | SU F2 INV19 | DcMs_Amp_12 | A | 30.5.2329
SUINV19JB2 | 14 | DC current input 13 | SU F2 INV19 | DcMs_Amp_13 | A | 30.5.2330
SUINV19JB2 | 15 | DC current input 14 | SU F2 INV19 | DcMs_Amp_14 | A | 30.5.2331
SUINV19JB2 | 16 | DC current input 15 | SU F2 INV19 | DcMs_Amp_15 | A | 30.5.2332
SUINV19JB2 | 17 | DC current input 16 | SU F2 INV19 | DcMs_Amp_16 | A | 30.5.2333
SUINV19JB2 | 18 | DC current input 1 | SU F2 INV19 | DcMs_Amp_01_F | A | 30.5.2334
SUINV19JB2 | 19 | DC current input 2 | SU F2 INV19 | DcMs_Amp_02_F | A | 30.5.2335
SUINV19JB2 | 20 | DC current input 3 | SU F2 INV19 | DcMs_Amp_03_F | A | 30.5.2336
SUINV19JB2 | 21 | DC current input 4 | SU F2 INV19 | DcMs_Amp_04_F | A | 30.5.2337
SUINV19JB2 | 22 | DC current input 5 | SU F2 INV19 | DcMs_Amp_05_F | A | 30.5.2338
SUINV19JB2 | 23 | DC current input 6 | SU F2 INV19 | DcMs_Amp_06_F | A | 30.5.2339
SUINV19JB2 | 24 | DC current input 7 | SU F2 INV19 | DcMs_Amp_07_F | A | 30.5.2340
SUINV19JB2 | 25 | DC current input 8 | SU F2 INV19 | DcMs_Amp_08_F | A | 30.5.2341
SUINV19JB2 | 26 | DC current input 9 | SU F2 INV19 | DcMs_Amp_09_F | A | 30.5.2342
SUINV19JB2 | 27 | DC current input 10 | SU F2 INV19 | DcMs_Amp_10_F | A | 30.5.2343
SUINV19JB2 | 28 | DC current input 11 | SU F2 INV19 | DcMs_Amp_11_F | A | 30.5.2344
SUINV19JB2 | 29 | DC current input 12 | SU F2 INV19 | DcMs_Amp_12_F | A | 30.5.2345
SUINV19JB2 | 30 | DC current input 13 | SU F2 INV19 | DcMs_Amp_13_F | A | 30.5.2346
SUINV19JB2 | 31 | DC current input 14 | SU F2 INV19 | DcMs_Amp_14_F | A | 30.5.2347
SUINV19JB2 | 32 | DC current input 15 | SU F2 INV19 | DcMs_Amp_15_F | A | 30.5.2348
SUINV19JB2 | 33 | DC current input 16 | SU F2 INV19 | DcMs_Amp_16_F | A | 30.5.2349
SUF2INV21 | 1 | DC voltage DC plus to DC minus | SU F2 INV21 | DcMs_Vol | V | 30.5.2350
SUF2INV21 | 2 | DC current inverter bridge 1 | SU F2 INV21 | DcMs_Amp_Stk1 | A | 30.5.2351
SUF2INV21 | 3 | DC current inverter bridge 2 | SU F2 INV21 | DcMs_Amp_Stk2 | A | 30.5.2352
SUF2INV21 | 4 | DC current inverter bridge 3 | SU F2 INV21 | DcMs_Amp_Stk3 | A | 30.5.2353
SUF2INV21 | 5 | DC current, total | SU F2 INV21 | DcMs_TotAmp | A | 30.5.2354
SUF2INV21 | 6 | DC power, total | SU F2 INV21 | DcMs_TotWatt | kW | 30.5.2355
SUF2INV21 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV21 | InvMs_DclVol_Stk1 | V | 30.5.2356
SUF2INV21 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV21 | InvMs_DclVol_Stk2 | V | 30.5.2357
SUF2INV21 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV21 | InvMs_DclVol_Stk3 | V | 30.5.2358
SUF2INV21 | 10 | AC current L1, total | SU F2 INV21 | InvMs_TotA_PhsA | A | 30.5.2359
SUF2INV21 | 11 | AC current L2, total | SU F2 INV21 | InvMs_TotA_PhsB | A | 30.5.2360
SUF2INV21 | 12 | AC current L3, total | SU F2 INV21 | InvMs_TotA_PhsC | A | 30.5.2361
SUF2INV21 | 13 | Power factor (cos phi) | SU F2 INV21 | InvMs_PF | "-" | 30.5.2362
SUF2INV21 | 14 | Apparent power, total | SU F2 INV21 | InvMs_TotVA | kVA | 30.5.2363
SUF2INV21 | 15 | Active power, total | SU F2 INV21 | InvMs_TotW | kW | 30.5.2364
SUF2INV21 | 16 | Reactive power, total | SU F2 INV21 | InvMs_TotVAr | kVAr | 30.5.2365
SUF2INV21 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV21 | GriMs_V_PhsAB | V | 30.5.2366
SUF2INV21 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV21 | GriMs_V_PhsBC | V | 30.5.2367
SUF2INV21 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV21 | GriMs_V_PhsCA | V | 30.5.2368
SUF2INV21 | 20 | Power frequency | SU F2 INV21 | GriMs_Hz | Hz | 30.5.2369
SUF2INV21 | 21 | Temperature in the AC range | SU F2 INV21 | TmpCab_Acc | °C | 30.5.2370
SUF2INV21 | 22 | Temperature in the DC range | SU F2 INV21 | TmpCab_Dcc | °C | 30.5.2371
SUF2INV21 | 23 | Temperature in the electronics area | SU F2 INV21 | TmpCab_Rio | °C | 30.5.2372
SUF2INV21 | 24 | Temperature in interior, maximum value | SU F2 INV21 | TmpCab_Max | °C | 30.5.2373
SUF2INV21 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV21 | TmpStk_IgbtMax | °C | 30.5.2374
SUF2INV21 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV21 | TmpStk_PcbMax | °C | 30.5.2375
SUF2INV21 | 27 | Outside temperature | SU F2 INV21 | TmpExl | ?C | 30.5.2376
SUF2INV21 | 28 | Temperature of the MV transformer | SU F2 INV21 | TmpTrf | °C | 30.5.2377
SUF2INV21 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV21 | DcSw1Stt | "-" | 30.5.2378
SUF2INV21 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV21 | DcSw2Stt | "-" | 30.5.2379
SUF2INV21 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV21 | DcSw3Stt | "-" | 30.5.2380
SUF2INV21 | 32 | Switching status of the AC circuit breaker | SU F2 INV21 | AcSwStt | "-" | 30.5.2381
SUF2INV21 | 33 | Switching state of the capacitor contactor | SU F2 INV21 | CapacSwStt | "-" | 30.5.2382
SUF2INV21 | 34 | Switching status of the pre-charging contactor | SU F2 INV21 | PrchrgSwStt | "-" | 30.5.2383
SUF2INV21 | 35 | Feed-in hours | SU F2 INV21 | Cnt_TotFeedTm | "-" | 30.5.2384
SUF2INV21 | 36 | Operating hours | SU F2 INV21 | Cnt_TotOpTm | "-" | 30.5.2385
SUF2INV21 | 37 | DC energy drawn, total | SU F2 INV21 | Cnt_TotWatthIn | MWh | 30.5.2386
SUF2INV21 | 38 | AC energy fed in, total | SU F2 INV21 | Cnt_TotWhOut | MWh | 30.5.2387
SUF2INV21 | 39 | DC energy drawn that day | SU F2 INV21 | Cnt_WatthIn | MWh | 30.5.2388
SUF2INV21 | 40 | AC energy fed in that day | SU F2 INV21 | Cnt_WhOut | MWh | 30.5.2389
SUF2INV21 | 41 | Operating hours of the interior fan 1 | SU F2 INV21 | Cnt_FanCab1Tm | "-" | 30.5.2390
SUF2INV21 | 42 | Operating hours of the interior fan 2 | SU F2 INV21 | Cnt_FanCab2Tm | "-" | 30.5.2391
SUF2INV21 | 43 | Operating hours of the inverter bridge fan | SU F2 INV21 | Cnt_FanStkTm | "-" | 30.5.2392
SUF2INV21 | 44 | Operating hours of the internal heating element | SU F2 INV21 | Cnt_HtCabTm | "-" | 30.5.2393
SUF2INV21 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV21 | Cnt_HtLoExlTmpTm | "-" | 30.5.2394
SUF2INV21 | 46 | Error location of the present error | SU F2 INV21 | ErrLcn | "-" | 30.5.2395
SUF2INV21 | 47 | Error status of the inverter | SU F2 INV21 | ErrStt | "-" | 30.5.2396
SUF2INV21 | 48 | Error number of the present error | SU F2 INV21 | ErrNo | "-" | 30.5.2397
SUF2INV21 | 49 | Operating state of the inverter | SU F2 INV21 | OpStt | "-" | 30.5.2398
SUF2INV21 | 50 | Switch status of the start-stop key switch | SU F2 INV21 | Rio_KeySw | "-" | 30.5.2399
SUF2INV21 | 51 | Waiting time for grid connection | SU F2 INV21 | WaitGriTm | s | 30.5.2400
SUF2INV21 | 52 | Inverter serial number | SU F2 INV21 | DevInf_SerNo | "-" | 30.5.2401
SUF2INV21 | 53 | Switching status of the GFDI | SU F2 INV21 | GfdiSwStt | "-" | 30.5.2402
SUF2INV21 | 54 | Active power, setpoint | SU F2 INV21 | WSpt | kW | 30.5.2403
SUF2INV21 | 55 | Maximum apparent power, setpoint | SU F2 INV21 | VAMaxSpt | kVA | 30.5.2404
SUF2INV21 | 56 | Reactive power, setpoint | SU F2 INV21 | VArSpt | kVAr | 30.5.2405
SUF2INV21 | 57 | Power factor cos (phi), setpoint | SU F2 INV21 | PFSpt | "-" | 30.5.2406
SUF2INV21 | 58 | Fast stop hermetic protection, pressure | SU F2 INV21 | TrfPro_Pres | "-" | 30.5.2407
SUF2INV21 | 59 | Fast stop hermetic protection, temperature | SU F2 INV21 | TrfPro_TmpTrp | "-" | 30.5.2408
SUF2INV21 | 60 | Hermetic protection, gas fill level | SU F2 INV21 | TrfPro_GasOilLev | "-" | 30.5.2409
SUF2INV21 | 61 | Hermetic pressure, temperature warning | SU F2 INV21 | TrfPro_TmpWrn | "-" | 30.5.2410
SUF2INV21 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV21 | TmpStk1_Igbt | °C | 30.5.2411
SUF2INV21 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV21 | TmpStk2_Igbt | °C | 30.5.2412
SUF2INV21 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV21 | TmpStk3_Igbt | °C | 30.5.2413
SUF2INV21 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV21 | TmpStk1_Pcb | ?C | 30.5.2414
SUF2INV21 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV21 | TmpStk2_Pcb | ?C | 30.5.2415
SUF2INV21 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV21 | TmpStk3_Pcb | ?C | 30.5.2416
SUF2INV21 | 68 | AC Energy Fed in the previous Day | SU F2 INV21 | Cnt_YstdWhOut | MWh | 30.5.2417
SUF2INV21 | 69 | CPU running time since system start | SU F2 INV21 | Cpu1UpTime | s | 30.5.2418
SUF2INV21 | 70 | Insulation resistance | SU F2 INV21 | PvGnd_RisIso | kOhm | 30.5.2419
SUF2INV21 | 71 | MV transformer pressure | SU F2 INV21 | PresTrf | "-" | 30.5.2420
SUF2INV21 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV21 | PresTrf_ErrStt | "-" | 30.5.2421
SUF2INV21 | 73 | DC voltage DC plus to DC minus | SU F2 INV21 | DcMs_Vol_F | V | 30.5.2422
SUF2INV21 | 74 | DC current inverter bridge 1 | SU F2 INV21 | DcMs_Amp_Stk1_F | A | 30.5.2423
SUF2INV21 | 75 | DC current inverter bridge 2 | SU F2 INV21 | DcMs_Amp_Stk2_F | A | 30.5.2424
SUF2INV21 | 76 | DC current inverter bridge 3 | SU F2 INV21 | DcMs_Amp_Stk3_F | A | 30.5.2425
SUF2INV21 | 77 | DC current, total | SU F2 INV21 | DcMs_TotAmp_F | A | 30.5.2426
SUF2INV21 | 78 | DC power, total | SU F2 INV21 | DcMs_TotWatt_F | kW | 30.5.2427
SUF2INV21 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV21 | InvMs_DclVol_Stk1_F | V | 30.5.2428
SUF2INV21 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV21 | InvMs_DclVol_Stk2_F | V | 30.5.2429
SUF2INV21 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV21 | InvMs_DclVol_Stk3_F | V | 30.5.2430
SUF2INV21 | 82 | AC current L1, total | SU F2 INV21 | InvMs_TotA_PhsA_F | A | 30.5.2431
SUF2INV21 | 83 | AC current L2, total | SU F2 INV21 | InvMs_TotA_PhsB_F | A | 30.5.2432
SUF2INV21 | 84 | AC current L3, total | SU F2 INV21 | InvMs_TotA_PhsC_F | A | 30.5.2433
SUF2INV21 | 85 | Power factor (cos phi) | SU F2 INV21 | InvMs_PF_F | "-" | 30.5.2434
SUF2INV21 | 86 | Active power, total | SU F2 INV21 | InvMs_TotW_F | kW | 30.5.2435
SUF2INV21 | 87 | Reactive power, total | SU F2 INV21 | InvMs_TotVAr_F | kVAr | 30.5.2436
SUF2INV21 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV21 | GriMs_V_PhsAB_F | V | 30.5.2437
SUF2INV21 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV21 | GriMs_V_PhsBC_F | V | 30.5.2438
SUF2INV21 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV21 | GriMs_V_PhsCA_F | V | 30.5.2439
SUF2INV21 | 91 | Power frequency | SU F2 INV21 | GriMs_Hz_F | Hz | 30.5.2440
SUF2INV21 | 92 | Temperature in the AC range | SU F2 INV21 | TmpCab_Acc_F | °C | 30.5.2441
SUF2INV21 | 93 | Temperature in the DC range | SU F2 INV21 | TmpCab_Dcc_F | °C | 30.5.2442
SUF2INV21 | 94 | Temperature in the electronics area | SU F2 INV21 | TmpCab_Rio_F | °C | 30.5.2443
SUF2INV21 | 95 | Temperature in interior, maximum value | SU F2 INV21 | TmpCab_Max_F | °C | 30.5.2444
SUF2INV21 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV21 | TmpStk_IgbtMax_F | °C | 30.5.2445
SUF2INV21 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV21 | TmpStk_PcbMax_F | °C | 30.5.2446
SUF2INV21 | 98 | Outside temperature | SU F2 INV21 | TmpExl_F | ?C | 30.5.2447
SUF2INV21 | 99 | Temperature of the MV transformer | SU F2 INV21 | TmpTrf_F | °C | 30.5.2448
SUF2INV21 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV21 | TmpStk1_Igbt_F | °C | 30.5.2449
SUF2INV21 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV21 | TmpStk2_Igbt_F | °C | 30.5.2450
SUF2INV21 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV21 | TmpStk3_Igbt_F | °C | 30.5.2451
SUF2INV21 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV21 | TmpStk1_Pcb_F | ?C | 30.5.2452
SUF2INV21 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV21 | TmpStk2_Pcb_F | ?C | 30.5.2453
SUF2INV21 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV21 | TmpStk3_Pcb_F | ?C | 30.5.2454
SUF2INV21 | 106 | MV transformer pressure | SU F2 INV21 | PresTrf_F | "-" | 30.5.2455
SUF2INV21 | 110 | Switching status of the DC load-break switch | SU F2 INV21 | DcSwStt | "-" | 30.5.2456
SUINV21JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV21 | Dat_UpdCnt_1 | "-" | 30.5.2457
SUINV21JB1 | 2 | DC current input 1 | SU F2 INV21 | DcMs_Amp_01 | A | 30.5.2458
SUINV21JB1 | 3 | DC current input 2 | SU F2 INV21 | DcMs_Amp_02 | A | 30.5.2459
SUINV21JB1 | 4 | DC current input 3 | SU F2 INV21 | DcMs_Amp_03 | A | 30.5.2460
SUINV21JB1 | 5 | DC current input 4 | SU F2 INV21 | DcMs_Amp_04 | A | 30.5.2461
SUINV21JB1 | 6 | DC current input 5 | SU F2 INV21 | DcMs_Amp_05 | A | 30.5.2462
SUINV21JB1 | 7 | DC current input 6 | SU F2 INV21 | DcMs_Amp_06 | A | 30.5.2463
SUINV21JB1 | 8 | DC current input 7 | SU F2 INV21 | DcMs_Amp_07 | A | 30.5.2464
SUINV21JB1 | 9 | DC current input 8 | SU F2 INV21 | DcMs_Amp_08 | A | 30.5.2465
SUINV21JB1 | 10 | DC current input 9 | SU F2 INV21 | DcMs_Amp_09 | A | 30.5.2466
SUINV21JB1 | 11 | DC current input 10 | SU F2 INV21 | DcMs_Amp_10 | A | 30.5.2467
SUINV21JB1 | 12 | DC current input 11 | SU F2 INV21 | DcMs_Amp_11 | A | 30.5.2468
SUINV21JB1 | 13 | DC current input 12 | SU F2 INV21 | DcMs_Amp_12 | A | 30.5.2469
SUINV21JB1 | 14 | DC current input 13 | SU F2 INV21 | DcMs_Amp_13 | A | 30.5.2470
SUINV21JB1 | 15 | DC current input 14 | SU F2 INV21 | DcMs_Amp_14 | A | 30.5.2471
SUINV21JB1 | 16 | DC current input 15 | SU F2 INV21 | DcMs_Amp_15 | A | 30.5.2472
SUINV21JB1 | 17 | DC current input 16 | SU F2 INV21 | DcMs_Amp_16 | A | 30.5.2473
SUINV21JB1 | 18 | DC current input 1 | SU F2 INV21 | DcMs_Amp_01_F | A | 30.5.2474
SUINV21JB1 | 19 | DC current input 2 | SU F2 INV21 | DcMs_Amp_02_F | A | 30.5.2475
SUINV21JB1 | 20 | DC current input 3 | SU F2 INV21 | DcMs_Amp_03_F | A | 30.5.2476
SUINV21JB1 | 21 | DC current input 4 | SU F2 INV21 | DcMs_Amp_04_F | A | 30.5.2477
SUINV21JB1 | 22 | DC current input 5 | SU F2 INV21 | DcMs_Amp_05_F | A | 30.5.2478
SUINV21JB1 | 23 | DC current input 6 | SU F2 INV21 | DcMs_Amp_06_F | A | 30.5.2479
SUINV21JB1 | 24 | DC current input 7 | SU F2 INV21 | DcMs_Amp_07_F | A | 30.5.2480
SUINV21JB1 | 25 | DC current input 8 | SU F2 INV21 | DcMs_Amp_08_F | A | 30.5.2481
SUINV21JB1 | 26 | DC current input 9 | SU F2 INV21 | DcMs_Amp_09_F | A | 30.5.2482
SUINV21JB1 | 27 | DC current input 10 | SU F2 INV21 | DcMs_Amp_10_F | A | 30.5.2483
SUINV21JB1 | 28 | DC current input 11 | SU F2 INV21 | DcMs_Amp_11_F | A | 30.5.2484
SUINV21JB1 | 29 | DC current input 12 | SU F2 INV21 | DcMs_Amp_12_F | A | 30.5.2485
SUINV21JB1 | 30 | DC current input 13 | SU F2 INV21 | DcMs_Amp_13_F | A | 30.5.2486
SUINV21JB1 | 31 | DC current input 14 | SU F2 INV21 | DcMs_Amp_14_F | A | 30.5.2487
SUINV21JB1 | 32 | DC current input 15 | SU F2 INV21 | DcMs_Amp_15_F | A | 30.5.2488
SUINV21JB1 | 33 | DC current input 16 | SU F2 INV21 | DcMs_Amp_16_F | A | 30.5.2489
SUINV21JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV21 | Dat_UpdCnt_1 | "-" | 30.5.2490
SUINV21JB2 | 2 | DC current input 1 | SU F2 INV21 | DcMs_Amp_01 | A | 30.5.2491
SUINV21JB2 | 3 | DC current input 2 | SU F2 INV21 | DcMs_Amp_02 | A | 30.5.2492
SUINV21JB2 | 4 | DC current input 3 | SU F2 INV21 | DcMs_Amp_03 | A | 30.5.2493
SUINV21JB2 | 5 | DC current input 4 | SU F2 INV21 | DcMs_Amp_04 | A | 30.5.2494
SUINV21JB2 | 6 | DC current input 5 | SU F2 INV21 | DcMs_Amp_05 | A | 30.5.2495
SUINV21JB2 | 7 | DC current input 6 | SU F2 INV21 | DcMs_Amp_06 | A | 30.5.2496
SUINV21JB2 | 8 | DC current input 7 | SU F2 INV21 | DcMs_Amp_07 | A | 30.5.2497
SUINV21JB2 | 9 | DC current input 8 | SU F2 INV21 | DcMs_Amp_08 | A | 30.5.2498
SUINV21JB2 | 10 | DC current input 9 | SU F2 INV21 | DcMs_Amp_09 | A | 30.5.2499
SUINV21JB2 | 11 | DC current input 10 | SU F2 INV21 | DcMs_Amp_10 | A | 30.5.2500
SUINV21JB2 | 12 | DC current input 11 | SU F2 INV21 | DcMs_Amp_11 | A | 30.5.2501
SUINV21JB2 | 13 | DC current input 12 | SU F2 INV21 | DcMs_Amp_12 | A | 30.5.2502
SUINV21JB2 | 14 | DC current input 13 | SU F2 INV21 | DcMs_Amp_13 | A | 30.5.2503
SUINV21JB2 | 15 | DC current input 14 | SU F2 INV21 | DcMs_Amp_14 | A | 30.5.2504
SUINV21JB2 | 16 | DC current input 15 | SU F2 INV21 | DcMs_Amp_15 | A | 30.5.2505
SUINV21JB2 | 17 | DC current input 16 | SU F2 INV21 | DcMs_Amp_16 | A | 30.5.2506
SUINV21JB2 | 18 | DC current input 1 | SU F2 INV21 | DcMs_Amp_01_F | A | 30.5.2507
SUINV21JB2 | 19 | DC current input 2 | SU F2 INV21 | DcMs_Amp_02_F | A | 30.5.2508
SUINV21JB2 | 20 | DC current input 3 | SU F2 INV21 | DcMs_Amp_03_F | A | 30.5.2509
SUINV21JB2 | 21 | DC current input 4 | SU F2 INV21 | DcMs_Amp_04_F | A | 30.5.2510
SUINV21JB2 | 22 | DC current input 5 | SU F2 INV21 | DcMs_Amp_05_F | A | 30.5.2511
SUINV21JB2 | 23 | DC current input 6 | SU F2 INV21 | DcMs_Amp_06_F | A | 30.5.2512
SUINV21JB2 | 24 | DC current input 7 | SU F2 INV21 | DcMs_Amp_07_F | A | 30.5.2513
SUINV21JB2 | 25 | DC current input 8 | SU F2 INV21 | DcMs_Amp_08_F | A | 30.5.2514
SUINV21JB2 | 26 | DC current input 9 | SU F2 INV21 | DcMs_Amp_09_F | A | 30.5.2515
SUINV21JB2 | 27 | DC current input 10 | SU F2 INV21 | DcMs_Amp_10_F | A | 30.5.2516
SUINV21JB2 | 28 | DC current input 11 | SU F2 INV21 | DcMs_Amp_11_F | A | 30.5.2517
SUINV21JB2 | 29 | DC current input 12 | SU F2 INV21 | DcMs_Amp_12_F | A | 30.5.2518
SUINV21JB2 | 30 | DC current input 13 | SU F2 INV21 | DcMs_Amp_13_F | A | 30.5.2519
SUINV21JB2 | 31 | DC current input 14 | SU F2 INV21 | DcMs_Amp_14_F | A | 30.5.2520
SUINV21JB2 | 32 | DC current input 15 | SU F2 INV21 | DcMs_Amp_15_F | A | 30.5.2521
SUINV21JB2 | 33 | DC current input 16 | SU F2 INV21 | DcMs_Amp_16_F | A | 30.5.2522
SUF2INV22 | 1 | DC voltage DC plus to DC minus | SU F2 INV22 | DcMs_Vol | V | 30.5.2523
SUF2INV22 | 2 | DC current inverter bridge 1 | SU F2 INV22 | DcMs_Amp_Stk1 | A | 30.5.2524
SUF2INV22 | 3 | DC current inverter bridge 2 | SU F2 INV22 | DcMs_Amp_Stk2 | A | 30.5.2525
SUF2INV22 | 4 | DC current inverter bridge 3 | SU F2 INV22 | DcMs_Amp_Stk3 | A | 30.5.2526
SUF2INV22 | 5 | DC current, total | SU F2 INV22 | DcMs_TotAmp | A | 30.5.2527
SUF2INV22 | 6 | DC power, total | SU F2 INV22 | DcMs_TotWatt | kW | 30.5.2528
SUF2INV22 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV22 | InvMs_DclVol_Stk1 | V | 30.5.2529
SUF2INV22 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV22 | InvMs_DclVol_Stk2 | V | 30.5.2530
SUF2INV22 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV22 | InvMs_DclVol_Stk3 | V | 30.5.2531
SUF2INV22 | 10 | AC current L1, total | SU F2 INV22 | InvMs_TotA_PhsA | A | 30.5.2532
SUF2INV22 | 11 | AC current L2, total | SU F2 INV22 | InvMs_TotA_PhsB | A | 30.5.2533
SUF2INV22 | 12 | AC current L3, total | SU F2 INV22 | InvMs_TotA_PhsC | A | 30.5.2534
SUF2INV22 | 13 | Power factor (cos phi) | SU F2 INV22 | InvMs_PF | "-" | 30.5.2535
SUF2INV22 | 14 | Apparent power, total | SU F2 INV22 | InvMs_TotVA | kVA | 30.5.2536
SUF2INV22 | 15 | Active power, total | SU F2 INV22 | InvMs_TotW | kW | 30.5.2537
SUF2INV22 | 16 | Reactive power, total | SU F2 INV22 | InvMs_TotVAr | kVAr | 30.5.2538
SUF2INV22 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV22 | GriMs_V_PhsAB | V | 30.5.2539
SUF2INV22 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV22 | GriMs_V_PhsBC | V | 30.5.2540
SUF2INV22 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV22 | GriMs_V_PhsCA | V | 30.5.2541
SUF2INV22 | 20 | Power frequency | SU F2 INV22 | GriMs_Hz | Hz | 30.5.2542
SUF2INV22 | 21 | Temperature in the AC range | SU F2 INV22 | TmpCab_Acc | °C | 30.5.2543
SUF2INV22 | 22 | Temperature in the DC range | SU F2 INV22 | TmpCab_Dcc | °C | 30.5.2544
SUF2INV22 | 23 | Temperature in the electronics area | SU F2 INV22 | TmpCab_Rio | °C | 30.5.2545
SUF2INV22 | 24 | Temperature in interior, maximum value | SU F2 INV22 | TmpCab_Max | °C | 30.5.2546
SUF2INV22 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV22 | TmpStk_IgbtMax | °C | 30.5.2547
SUF2INV22 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV22 | TmpStk_PcbMax | °C | 30.5.2548
SUF2INV22 | 27 | Outside temperature | SU F2 INV22 | TmpExl | ?C | 30.5.2549
SUF2INV22 | 28 | Temperature of the MV transformer | SU F2 INV22 | TmpTrf | °C | 30.5.2550
SUF2INV22 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV22 | DcSw1Stt | "-" | 30.5.2551
SUF2INV22 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV22 | DcSw2Stt | "-" | 30.5.2552
SUF2INV22 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV22 | DcSw3Stt | "-" | 30.5.2553
SUF2INV22 | 32 | Switching status of the AC circuit breaker | SU F2 INV22 | AcSwStt | "-" | 30.5.2554
SUF2INV22 | 33 | Switching state of the capacitor contactor | SU F2 INV22 | CapacSwStt | "-" | 30.5.2555
SUF2INV22 | 34 | Switching status of the pre-charging contactor | SU F2 INV22 | PrchrgSwStt | "-" | 30.5.2556
SUF2INV22 | 35 | Feed-in hours | SU F2 INV22 | Cnt_TotFeedTm | "-" | 30.5.2557
SUF2INV22 | 36 | Operating hours | SU F2 INV22 | Cnt_TotOpTm | "-" | 30.5.2558
SUF2INV22 | 37 | DC energy drawn, total | SU F2 INV22 | Cnt_TotWatthIn | MWh | 30.5.2559
SUF2INV22 | 38 | AC energy fed in, total | SU F2 INV22 | Cnt_TotWhOut | MWh | 30.5.2560
SUF2INV22 | 39 | DC energy drawn that day | SU F2 INV22 | Cnt_WatthIn | MWh | 30.5.2561
SUF2INV22 | 40 | AC energy fed in that day | SU F2 INV22 | Cnt_WhOut | MWh | 30.5.2562
SUF2INV22 | 41 | Operating hours of the interior fan 1 | SU F2 INV22 | Cnt_FanCab1Tm | "-" | 30.5.2563
SUF2INV22 | 42 | Operating hours of the interior fan 2 | SU F2 INV22 | Cnt_FanCab2Tm | "-" | 30.5.2564
SUF2INV22 | 43 | Operating hours of the inverter bridge fan | SU F2 INV22 | Cnt_FanStkTm | "-" | 30.5.2565
SUF2INV22 | 44 | Operating hours of the internal heating element | SU F2 INV22 | Cnt_HtCabTm | "-" | 30.5.2566
SUF2INV22 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV22 | Cnt_HtLoExlTmpTm | "-" | 30.5.2567
SUF2INV22 | 46 | Error location of the present error | SU F2 INV22 | ErrLcn | "-" | 30.5.2568
SUF2INV22 | 47 | Error status of the inverter | SU F2 INV22 | ErrStt | "-" | 30.5.2569
SUF2INV22 | 48 | Error number of the present error | SU F2 INV22 | ErrNo | "-" | 30.5.2570
SUF2INV22 | 49 | Operating state of the inverter | SU F2 INV22 | OpStt | "-" | 30.5.2571
SUF2INV22 | 50 | Switch status of the start-stop key switch | SU F2 INV22 | Rio_KeySw | "-" | 30.5.2572
SUF2INV22 | 51 | Waiting time for grid connection | SU F2 INV22 | WaitGriTm | s | 30.5.2573
SUF2INV22 | 52 | Inverter serial number | SU F2 INV22 | DevInf_SerNo | "-" | 30.5.2574
SUF2INV22 | 53 | Switching status of the GFDI | SU F2 INV22 | GfdiSwStt | "-" | 30.5.2575
SUF2INV22 | 54 | Active power, setpoint | SU F2 INV22 | WSpt | kW | 30.5.2576
SUF2INV22 | 55 | Maximum apparent power, setpoint | SU F2 INV22 | VAMaxSpt | kVA | 30.5.2577
SUF2INV22 | 56 | Reactive power, setpoint | SU F2 INV22 | VArSpt | kVAr | 30.5.2578
SUF2INV22 | 57 | Power factor cos (phi), setpoint | SU F2 INV22 | PFSpt | "-" | 30.5.2579
SUF2INV22 | 58 | Fast stop hermetic protection, pressure | SU F2 INV22 | TrfPro_Pres | "-" | 30.5.2580
SUF2INV22 | 59 | Fast stop hermetic protection, temperature | SU F2 INV22 | TrfPro_TmpTrp | "-" | 30.5.2581
SUF2INV22 | 60 | Hermetic protection, gas fill level | SU F2 INV22 | TrfPro_GasOilLev | "-" | 30.5.2582
SUF2INV22 | 61 | Hermetic pressure, temperature warning | SU F2 INV22 | TrfPro_TmpWrn | "-" | 30.5.2583
SUF2INV22 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV22 | TmpStk1_Igbt | °C | 30.5.2584
SUF2INV22 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV22 | TmpStk2_Igbt | °C | 30.5.2585
SUF2INV22 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV22 | TmpStk3_Igbt | °C | 30.5.2586
SUF2INV22 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV22 | TmpStk1_Pcb | ?C | 30.5.2587
SUF2INV22 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV22 | TmpStk2_Pcb | ?C | 30.5.2588
SUF2INV22 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV22 | TmpStk3_Pcb | ?C | 30.5.2589
SUF2INV22 | 68 | AC Energy Fed in the previous Day | SU F2 INV22 | Cnt_YstdWhOut | MWh | 30.5.2590
SUF2INV22 | 69 | CPU running time since system start | SU F2 INV22 | Cpu1UpTime | s | 30.5.2591
SUF2INV22 | 70 | Insulation resistance | SU F2 INV22 | PvGnd_RisIso | kOhm | 30.5.2592
SUF2INV22 | 71 | MV transformer pressure | SU F2 INV22 | PresTrf | "-" | 30.5.2593
SUF2INV22 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV22 | PresTrf_ErrStt | "-" | 30.5.2594
SUF2INV22 | 73 | DC voltage DC plus to DC minus | SU F2 INV22 | DcMs_Vol_F | V | 30.5.2595
SUF2INV22 | 74 | DC current inverter bridge 1 | SU F2 INV22 | DcMs_Amp_Stk1_F | A | 30.5.2596
SUF2INV22 | 75 | DC current inverter bridge 2 | SU F2 INV22 | DcMs_Amp_Stk2_F | A | 30.5.2597
SUF2INV22 | 76 | DC current inverter bridge 3 | SU F2 INV22 | DcMs_Amp_Stk3_F | A | 30.5.2598
SUF2INV22 | 77 | DC current, total | SU F2 INV22 | DcMs_TotAmp_F | A | 30.5.2599
SUF2INV22 | 78 | DC power, total | SU F2 INV22 | DcMs_TotWatt_F | kW | 30.5.2600
SUF2INV22 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV22 | InvMs_DclVol_Stk1_F | V | 30.5.2601
SUF2INV22 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV22 | InvMs_DclVol_Stk2_F | V | 30.5.2602
SUF2INV22 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV22 | InvMs_DclVol_Stk3_F | V | 30.5.2603
SUF2INV22 | 82 | AC current L1, total | SU F2 INV22 | InvMs_TotA_PhsA_F | A | 30.5.2604
SUF2INV22 | 83 | AC current L2, total | SU F2 INV22 | InvMs_TotA_PhsB_F | A | 30.5.2605
SUF2INV22 | 84 | AC current L3, total | SU F2 INV22 | InvMs_TotA_PhsC_F | A | 30.5.2606
SUF2INV22 | 85 | Power factor (cos phi) | SU F2 INV22 | InvMs_PF_F | "-" | 30.5.2607
SUF2INV22 | 86 | Active power, total | SU F2 INV22 | InvMs_TotW_F | kW | 30.5.2608
SUF2INV22 | 87 | Reactive power, total | SU F2 INV22 | InvMs_TotVAr_F | kVAr | 30.5.2609
SUF2INV22 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV22 | GriMs_V_PhsAB_F | V | 30.5.2610
SUF2INV22 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV22 | GriMs_V_PhsBC_F | V | 30.5.2611
SUF2INV22 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV22 | GriMs_V_PhsCA_F | V | 30.5.2612
SUF2INV22 | 91 | Power frequency | SU F2 INV22 | GriMs_Hz_F | Hz | 30.5.2613
SUF2INV22 | 92 | Temperature in the AC range | SU F2 INV22 | TmpCab_Acc_F | °C | 30.5.2614
SUF2INV22 | 93 | Temperature in the DC range | SU F2 INV22 | TmpCab_Dcc_F | °C | 30.5.2615
SUF2INV22 | 94 | Temperature in the electronics area | SU F2 INV22 | TmpCab_Rio_F | °C | 30.5.2616
SUF2INV22 | 95 | Temperature in interior, maximum value | SU F2 INV22 | TmpCab_Max_F | °C | 30.5.2617
SUF2INV22 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV22 | TmpStk_IgbtMax_F | °C | 30.5.2618
SUF2INV22 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV22 | TmpStk_PcbMax_F | °C | 30.5.2619
SUF2INV22 | 98 | Outside temperature | SU F2 INV22 | TmpExl_F | ?C | 30.5.2620
SUF2INV22 | 99 | Temperature of the MV transformer | SU F2 INV22 | TmpTrf_F | °C | 30.5.2621
SUF2INV22 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV22 | TmpStk1_Igbt_F | °C | 30.5.2622
SUF2INV22 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV22 | TmpStk2_Igbt_F | °C | 30.5.2623
SUF2INV22 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV22 | TmpStk3_Igbt_F | °C | 30.5.2624
SUF2INV22 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV22 | TmpStk1_Pcb_F | ?C | 30.5.2625
SUF2INV22 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV22 | TmpStk2_Pcb_F | ?C | 30.5.2626
SUF2INV22 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV22 | TmpStk3_Pcb_F | ?C | 30.5.2627
SUF2INV22 | 106 | MV transformer pressure | SU F2 INV22 | PresTrf_F | "-" | 30.5.2628
SUF2INV22 | 110 | Switching status of the DC load-break switch | SU F2 INV22 | DcSwStt | "-" | 30.5.2629
SUINV22JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV22 | Dat_UpdCnt_1 | "-" | 30.5.2630
SUINV22JB1 | 2 | DC current input 1 | SU F2 INV22 | DcMs_Amp_01 | A | 30.5.2631
SUINV22JB1 | 3 | DC current input 2 | SU F2 INV22 | DcMs_Amp_02 | A | 30.5.2632
SUINV22JB1 | 4 | DC current input 3 | SU F2 INV22 | DcMs_Amp_03 | A | 30.5.2633
SUINV22JB1 | 5 | DC current input 4 | SU F2 INV22 | DcMs_Amp_04 | A | 30.5.2634
SUINV22JB1 | 6 | DC current input 5 | SU F2 INV22 | DcMs_Amp_05 | A | 30.5.2635
SUINV22JB1 | 7 | DC current input 6 | SU F2 INV22 | DcMs_Amp_06 | A | 30.5.2636
SUINV22JB1 | 8 | DC current input 7 | SU F2 INV22 | DcMs_Amp_07 | A | 30.5.2637
SUINV22JB1 | 9 | DC current input 8 | SU F2 INV22 | DcMs_Amp_08 | A | 30.5.2638
SUINV22JB1 | 10 | DC current input 9 | SU F2 INV22 | DcMs_Amp_09 | A | 30.5.2639
SUINV22JB1 | 11 | DC current input 10 | SU F2 INV22 | DcMs_Amp_10 | A | 30.5.2640
SUINV22JB1 | 12 | DC current input 11 | SU F2 INV22 | DcMs_Amp_11 | A | 30.5.2641
SUINV22JB1 | 13 | DC current input 12 | SU F2 INV22 | DcMs_Amp_12 | A | 30.5.2642
SUINV22JB1 | 14 | DC current input 13 | SU F2 INV22 | DcMs_Amp_13 | A | 30.5.2643
SUINV22JB1 | 15 | DC current input 14 | SU F2 INV22 | DcMs_Amp_14 | A | 30.5.2644
SUINV22JB1 | 16 | DC current input 15 | SU F2 INV22 | DcMs_Amp_15 | A | 30.5.2645
SUINV22JB1 | 17 | DC current input 16 | SU F2 INV22 | DcMs_Amp_16 | A | 30.5.2646
SUINV22JB1 | 18 | DC current input 1 | SU F2 INV22 | DcMs_Amp_01_F | A | 30.5.2647
SUINV22JB1 | 19 | DC current input 2 | SU F2 INV22 | DcMs_Amp_02_F | A | 30.5.2648
SUINV22JB1 | 20 | DC current input 3 | SU F2 INV22 | DcMs_Amp_03_F | A | 30.5.2649
SUINV22JB1 | 21 | DC current input 4 | SU F2 INV22 | DcMs_Amp_04_F | A | 30.5.2650
SUINV22JB1 | 22 | DC current input 5 | SU F2 INV22 | DcMs_Amp_05_F | A | 30.5.2651
SUINV22JB1 | 23 | DC current input 6 | SU F2 INV22 | DcMs_Amp_06_F | A | 30.5.2652
SUINV22JB1 | 24 | DC current input 7 | SU F2 INV22 | DcMs_Amp_07_F | A | 30.5.2653
SUINV22JB1 | 25 | DC current input 8 | SU F2 INV22 | DcMs_Amp_08_F | A | 30.5.2654
SUINV22JB1 | 26 | DC current input 9 | SU F2 INV22 | DcMs_Amp_09_F | A | 30.5.2655
SUINV22JB1 | 27 | DC current input 10 | SU F2 INV22 | DcMs_Amp_10_F | A | 30.5.2656
SUINV22JB1 | 28 | DC current input 11 | SU F2 INV22 | DcMs_Amp_11_F | A | 30.5.2657
SUINV22JB1 | 29 | DC current input 12 | SU F2 INV22 | DcMs_Amp_12_F | A | 30.5.2658
SUINV22JB1 | 30 | DC current input 13 | SU F2 INV22 | DcMs_Amp_13_F | A | 30.5.2659
SUINV22JB1 | 31 | DC current input 14 | SU F2 INV22 | DcMs_Amp_14_F | A | 30.5.2660
SUINV22JB1 | 32 | DC current input 15 | SU F2 INV22 | DcMs_Amp_15_F | A | 30.5.2661
SUINV22JB1 | 33 | DC current input 16 | SU F2 INV22 | DcMs_Amp_16_F | A | 30.5.2662
SUINV22JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV22 | Dat_UpdCnt_1 | "-" | 30.5.2663
SUINV22JB2 | 2 | DC current input 1 | SU F2 INV22 | DcMs_Amp_01 | A | 30.5.2664
SUINV22JB2 | 3 | DC current input 2 | SU F2 INV22 | DcMs_Amp_02 | A | 30.5.2665
SUINV22JB2 | 4 | DC current input 3 | SU F2 INV22 | DcMs_Amp_03 | A | 30.5.2666
SUINV22JB2 | 5 | DC current input 4 | SU F2 INV22 | DcMs_Amp_04 | A | 30.5.2667
SUINV22JB2 | 6 | DC current input 5 | SU F2 INV22 | DcMs_Amp_05 | A | 30.5.2668
SUINV22JB2 | 7 | DC current input 6 | SU F2 INV22 | DcMs_Amp_06 | A | 30.5.2669
SUINV22JB2 | 8 | DC current input 7 | SU F2 INV22 | DcMs_Amp_07 | A | 30.5.2670
SUINV22JB2 | 9 | DC current input 8 | SU F2 INV22 | DcMs_Amp_08 | A | 30.5.2671
SUINV22JB2 | 10 | DC current input 9 | SU F2 INV22 | DcMs_Amp_09 | A | 30.5.2672
SUINV22JB2 | 11 | DC current input 10 | SU F2 INV22 | DcMs_Amp_10 | A | 30.5.2673
SUINV22JB2 | 12 | DC current input 11 | SU F2 INV22 | DcMs_Amp_11 | A | 30.5.2674
SUINV22JB2 | 13 | DC current input 12 | SU F2 INV22 | DcMs_Amp_12 | A | 30.5.2675
SUINV22JB2 | 14 | DC current input 13 | SU F2 INV22 | DcMs_Amp_13 | A | 30.5.2676
SUINV22JB2 | 15 | DC current input 14 | SU F2 INV22 | DcMs_Amp_14 | A | 30.5.2677
SUINV22JB2 | 16 | DC current input 15 | SU F2 INV22 | DcMs_Amp_15 | A | 30.5.2678
SUINV22JB2 | 17 | DC current input 16 | SU F2 INV22 | DcMs_Amp_16 | A | 30.5.2679
SUINV22JB2 | 18 | DC current input 1 | SU F2 INV22 | DcMs_Amp_01_F | A | 30.5.2680
SUINV22JB2 | 19 | DC current input 2 | SU F2 INV22 | DcMs_Amp_02_F | A | 30.5.2681
SUINV22JB2 | 20 | DC current input 3 | SU F2 INV22 | DcMs_Amp_03_F | A | 30.5.2682
SUINV22JB2 | 21 | DC current input 4 | SU F2 INV22 | DcMs_Amp_04_F | A | 30.5.2683
SUINV22JB2 | 22 | DC current input 5 | SU F2 INV22 | DcMs_Amp_05_F | A | 30.5.2684
SUINV22JB2 | 23 | DC current input 6 | SU F2 INV22 | DcMs_Amp_06_F | A | 30.5.2685
SUINV22JB2 | 24 | DC current input 7 | SU F2 INV22 | DcMs_Amp_07_F | A | 30.5.2686
SUINV22JB2 | 25 | DC current input 8 | SU F2 INV22 | DcMs_Amp_08_F | A | 30.5.2687
SUINV22JB2 | 26 | DC current input 9 | SU F2 INV22 | DcMs_Amp_09_F | A | 30.5.2688
SUINV22JB2 | 27 | DC current input 10 | SU F2 INV22 | DcMs_Amp_10_F | A | 30.5.2689
SUINV22JB2 | 28 | DC current input 11 | SU F2 INV22 | DcMs_Amp_11_F | A | 30.5.2690
SUINV22JB2 | 29 | DC current input 12 | SU F2 INV22 | DcMs_Amp_12_F | A | 30.5.2691
SUINV22JB2 | 30 | DC current input 13 | SU F2 INV22 | DcMs_Amp_13_F | A | 30.5.2692
SUINV22JB2 | 31 | DC current input 14 | SU F2 INV22 | DcMs_Amp_14_F | A | 30.5.2693
SUINV22JB2 | 32 | DC current input 15 | SU F2 INV22 | DcMs_Amp_15_F | A | 30.5.2694
SUINV22JB2 | 33 | DC current input 16 | SU F2 INV22 | DcMs_Amp_16_F | A | 30.5.2695
SUF2INV23 | 1 | DC voltage DC plus to DC minus | SU F2 INV23 | DcMs_Vol | V | 30.5.2696
SUF2INV23 | 2 | DC current inverter bridge 1 | SU F2 INV23 | DcMs_Amp_Stk1 | A | 30.5.2697
SUF2INV23 | 3 | DC current inverter bridge 2 | SU F2 INV23 | DcMs_Amp_Stk2 | A | 30.5.2698
SUF2INV23 | 4 | DC current inverter bridge 3 | SU F2 INV23 | DcMs_Amp_Stk3 | A | 30.5.2699
SUF2INV23 | 5 | DC current, total | SU F2 INV23 | DcMs_TotAmp | A | 30.5.2700
SUF2INV23 | 6 | DC power, total | SU F2 INV23 | DcMs_TotWatt | kW | 30.5.2701
SUF2INV23 | 7 | DC voltage of the inverter bridge 1 | SU F2 INV23 | InvMs_DclVol_Stk1 | V | 30.5.2702
SUF2INV23 | 8 | DC voltage of the inverter bridge 2 | SU F2 INV23 | InvMs_DclVol_Stk2 | V | 30.5.2703
SUF2INV23 | 9 | DC voltage of the inverter bridge 3 | SU F2 INV23 | InvMs_DclVol_Stk3 | V | 30.5.2704
SUF2INV23 | 10 | AC current L1, total | SU F2 INV23 | InvMs_TotA_PhsA | A | 30.5.2705
SUF2INV23 | 11 | AC current L2, total | SU F2 INV23 | InvMs_TotA_PhsB | A | 30.5.2706
SUF2INV23 | 12 | AC current L3, total | SU F2 INV23 | InvMs_TotA_PhsC | A | 30.5.2707
SUF2INV23 | 13 | Power factor (cos phi) | SU F2 INV23 | InvMs_PF | "-" | 30.5.2708
SUF2INV23 | 14 | Apparent power, total | SU F2 INV23 | InvMs_TotVA | kVA | 30.5.2709
SUF2INV23 | 15 | Active power, total | SU F2 INV23 | InvMs_TotW | kW | 30.5.2710
SUF2INV23 | 16 | Reactive power, total | SU F2 INV23 | InvMs_TotVAr | kVAr | 30.5.2711
SUF2INV23 | 17 | Line-to-line voltage L1-L2, utility grid | SU F2 INV23 | GriMs_V_PhsAB | V | 30.5.2712
SUF2INV23 | 18 | Line-to-line voltage L2-L3, utility grid | SU F2 INV23 | GriMs_V_PhsBC | V | 30.5.2713
SUF2INV23 | 19 | Line-to-line voltage L3-L1, utility grid | SU F2 INV23 | GriMs_V_PhsCA | V | 30.5.2714
SUF2INV23 | 20 | Power frequency | SU F2 INV23 | GriMs_Hz | Hz | 30.5.2715
SUF2INV23 | 21 | Temperature in the AC range | SU F2 INV23 | TmpCab_Acc | °C | 30.5.2716
SUF2INV23 | 22 | Temperature in the DC range | SU F2 INV23 | TmpCab_Dcc | °C | 30.5.2717
SUF2INV23 | 23 | Temperature in the electronics area | SU F2 INV23 | TmpCab_Rio | °C | 30.5.2718
SUF2INV23 | 24 | Temperature in interior, maximum value | SU F2 INV23 | TmpCab_Max | °C | 30.5.2719
SUF2INV23 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV23 | TmpStk_IgbtMax | °C | 30.5.2720
SUF2INV23 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV23 | TmpStk_PcbMax | °C | 30.5.2721
SUF2INV23 | 27 | Outside temperature | SU F2 INV23 | TmpExl | ?C | 30.5.2722
SUF2INV23 | 28 | Temperature of the MV transformer | SU F2 INV23 | TmpTrf | °C | 30.5.2723
SUF2INV23 | 29 | Switching status of the DC load-break switch 1 | SU F2 INV23 | DcSw1Stt | "-" | 30.5.2724
SUF2INV23 | 30 | Switching status of the DC load-break switch 2 | SU F2 INV23 | DcSw2Stt | "-" | 30.5.2725
SUF2INV23 | 31 | Switching status of the DC load-break switch 3 | SU F2 INV23 | DcSw3Stt | "-" | 30.5.2726
SUF2INV23 | 32 | Switching status of the AC circuit breaker | SU F2 INV23 | AcSwStt | "-" | 30.5.2727
SUF2INV23 | 33 | Switching state of the capacitor contactor | SU F2 INV23 | CapacSwStt | "-" | 30.5.2728
SUF2INV23 | 34 | Switching status of the pre-charging contactor | SU F2 INV23 | PrchrgSwStt | "-" | 30.5.2729
SUF2INV23 | 35 | Feed-in hours | SU F2 INV23 | Cnt_TotFeedTm | "-" | 30.5.2730
SUF2INV23 | 36 | Operating hours | SU F2 INV23 | Cnt_TotOpTm | "-" | 30.5.2731
SUF2INV23 | 37 | DC energy drawn, total | SU F2 INV23 | Cnt_TotWatthIn | MWh | 30.5.2732
SUF2INV23 | 38 | AC energy fed in, total | SU F2 INV23 | Cnt_TotWhOut | MWh | 30.5.2733
SUF2INV23 | 39 | DC energy drawn that day | SU F2 INV23 | Cnt_WatthIn | MWh | 30.5.2734
SUF2INV23 | 40 | AC energy fed in that day | SU F2 INV23 | Cnt_WhOut | MWh | 30.5.2735
SUF2INV23 | 41 | Operating hours of the interior fan 1 | SU F2 INV23 | Cnt_FanCab1Tm | "-" | 30.5.2736
SUF2INV23 | 42 | Operating hours of the interior fan 2 | SU F2 INV23 | Cnt_FanCab2Tm | "-" | 30.5.2737
SUF2INV23 | 43 | Operating hours of the inverter bridge fan | SU F2 INV23 | Cnt_FanStkTm | "-" | 30.5.2738
SUF2INV23 | 44 | Operating hours of the internal heating element | SU F2 INV23 | Cnt_HtCabTm | "-" | 30.5.2739
SUF2INV23 | 45 | Operating hours of the -40?C internal heating element | SU F2 INV23 | Cnt_HtLoExlTmpTm | "-" | 30.5.2740
SUF2INV23 | 46 | Error location of the present error | SU F2 INV23 | ErrLcn | "-" | 30.5.2741
SUF2INV23 | 47 | Error status of the inverter | SU F2 INV23 | ErrStt | "-" | 30.5.2742
SUF2INV23 | 48 | Error number of the present error | SU F2 INV23 | ErrNo | "-" | 30.5.2743
SUF2INV23 | 49 | Operating state of the inverter | SU F2 INV23 | OpStt | "-" | 30.5.2744
SUF2INV23 | 50 | Switch status of the start-stop key switch | SU F2 INV23 | Rio_KeySw | "-" | 30.5.2745
SUF2INV23 | 51 | Waiting time for grid connection | SU F2 INV23 | WaitGriTm | s | 30.5.2746
SUF2INV23 | 52 | Inverter serial number | SU F2 INV23 | DevInf_SerNo | "-" | 30.5.2747
SUF2INV23 | 53 | Switching status of the GFDI | SU F2 INV23 | GfdiSwStt | "-" | 30.5.2748
SUF2INV23 | 54 | Active power, setpoint | SU F2 INV23 | WSpt | kW | 30.5.2749
SUF2INV23 | 55 | Maximum apparent power, setpoint | SU F2 INV23 | VAMaxSpt | kVA | 30.5.2750
SUF2INV23 | 56 | Reactive power, setpoint | SU F2 INV23 | VArSpt | kVAr | 30.5.2751
SUF2INV23 | 57 | Power factor cos (phi), setpoint | SU F2 INV23 | PFSpt | "-" | 30.5.2752
SUF2INV23 | 58 | Fast stop hermetic protection, pressure | SU F2 INV23 | TrfPro_Pres | "-" | 30.5.2753
SUF2INV23 | 59 | Fast stop hermetic protection, temperature | SU F2 INV23 | TrfPro_TmpTrp | "-" | 30.5.2754
SUF2INV23 | 60 | Hermetic protection, gas fill level | SU F2 INV23 | TrfPro_GasOilLev | "-" | 30.5.2755
SUF2INV23 | 61 | Hermetic pressure, temperature warning | SU F2 INV23 | TrfPro_TmpWrn | "-" | 30.5.2756
SUF2INV23 | 62 | Temperature of inverter bridge 1 (switch) | SU F2 INV23 | TmpStk1_Igbt | °C | 30.5.2757
SUF2INV23 | 63 | Temperature of inverter bridge 2 (switch) | SU F2 INV23 | TmpStk2_Igbt | °C | 30.5.2758
SUF2INV23 | 64 | Temperature of inverter bridge 3 (switch) | SU F2 INV23 | TmpStk3_Igbt | °C | 30.5.2759
SUF2INV23 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV23 | TmpStk1_Pcb | ?C | 30.5.2760
SUF2INV23 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV23 | TmpStk2_Pcb | ?C | 30.5.2761
SUF2INV23 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV23 | TmpStk3_Pcb | ?C | 30.5.2762
SUF2INV23 | 68 | AC Energy Fed in the previous Day | SU F2 INV23 | Cnt_YstdWhOut | MWh | 30.5.2763
SUF2INV23 | 69 | CPU running time since system start | SU F2 INV23 | Cpu1UpTime | s | 30.5.2764
SUF2INV23 | 70 | Insulation resistance | SU F2 INV23 | PvGnd_RisIso | kOhm | 30.5.2765
SUF2INV23 | 71 | MV transformer pressure | SU F2 INV23 | PresTrf | "-" | 30.5.2766
SUF2INV23 | 72 | Error status of MV transformer pressure monitoring | SU F2 INV23 | PresTrf_ErrStt | "-" | 30.5.2767
SUF2INV23 | 73 | DC voltage DC plus to DC minus | SU F2 INV23 | DcMs_Vol_F | V | 30.5.2768
SUF2INV23 | 74 | DC current inverter bridge 1 | SU F2 INV23 | DcMs_Amp_Stk1_F | A | 30.5.2769
SUF2INV23 | 75 | DC current inverter bridge 2 | SU F2 INV23 | DcMs_Amp_Stk2_F | A | 30.5.2770
SUF2INV23 | 76 | DC current inverter bridge 3 | SU F2 INV23 | DcMs_Amp_Stk3_F | A | 30.5.2771
SUF2INV23 | 77 | DC current, total | SU F2 INV23 | DcMs_TotAmp_F | A | 30.5.2772
SUF2INV23 | 78 | DC power, total | SU F2 INV23 | DcMs_TotWatt_F | kW | 30.5.2773
SUF2INV23 | 79 | DC voltage of the inverter bridge 1 | SU F2 INV23 | InvMs_DclVol_Stk1_F | V | 30.5.2774
SUF2INV23 | 80 | DC voltage of the inverter bridge 2 | SU F2 INV23 | InvMs_DclVol_Stk2_F | V | 30.5.2775
SUF2INV23 | 81 | DC voltage of the inverter bridge 3 | SU F2 INV23 | InvMs_DclVol_Stk3_F | V | 30.5.2776
SUF2INV23 | 82 | AC current L1, total | SU F2 INV23 | InvMs_TotA_PhsA_F | A | 30.5.2777
SUF2INV23 | 83 | AC current L2, total | SU F2 INV23 | InvMs_TotA_PhsB_F | A | 30.5.2778
SUF2INV23 | 84 | AC current L3, total | SU F2 INV23 | InvMs_TotA_PhsC_F | A | 30.5.2779
SUF2INV23 | 85 | Power factor (cos phi) | SU F2 INV23 | InvMs_PF_F | "-" | 30.5.2780
SUF2INV23 | 86 | Active power, total | SU F2 INV23 | InvMs_TotW_F | kW | 30.5.2781
SUF2INV23 | 87 | Reactive power, total | SU F2 INV23 | InvMs_TotVAr_F | kVAr | 30.5.2782
SUF2INV23 | 88 | Line-to-line voltage L1-L2, utility grid | SU F2 INV23 | GriMs_V_PhsAB_F | V | 30.5.2783
SUF2INV23 | 89 | Line-to-line voltage L2-L3, utility grid | SU F2 INV23 | GriMs_V_PhsBC_F | V | 30.5.2784
SUF2INV23 | 90 | Line-to-line voltage L3-L1, utility grid | SU F2 INV23 | GriMs_V_PhsCA_F | V | 30.5.2785
SUF2INV23 | 91 | Power frequency | SU F2 INV23 | GriMs_Hz_F | Hz | 30.5.2786
SUF2INV23 | 92 | Temperature in the AC range | SU F2 INV23 | TmpCab_Acc_F | °C | 30.5.2787
SUF2INV23 | 93 | Temperature in the DC range | SU F2 INV23 | TmpCab_Dcc_F | °C | 30.5.2788
SUF2INV23 | 94 | Temperature in the electronics area | SU F2 INV23 | TmpCab_Rio_F | °C | 30.5.2789
SUF2INV23 | 95 | Temperature in interior, maximum value | SU F2 INV23 | TmpCab_Max_F | °C | 30.5.2790
SUF2INV23 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F2 INV23 | TmpStk_IgbtMax_F | °C | 30.5.2791
SUF2INV23 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F2 INV23 | TmpStk_PcbMax_F | °C | 30.5.2792
SUF2INV23 | 98 | Outside temperature | SU F2 INV23 | TmpExl_F | ?C | 30.5.2793
SUF2INV23 | 99 | Temperature of the MV transformer | SU F2 INV23 | TmpTrf_F | °C | 30.5.2794
SUF2INV23 | 100 | Temperature of inverter bridge 1 (switch) | SU F2 INV23 | TmpStk1_Igbt_F | °C | 30.5.2795
SUF2INV23 | 101 | Temperature of inverter bridge 2 (switch) | SU F2 INV23 | TmpStk2_Igbt_F | °C | 30.5.2796
SUF2INV23 | 102 | Temperature of inverter bridge 3 (switch) | SU F2 INV23 | TmpStk3_Igbt_F | °C | 30.5.2797
SUF2INV23 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F2 INV23 | TmpStk1_Pcb_F | ?C | 30.5.2798
SUF2INV23 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F2 INV23 | TmpStk2_Pcb_F | ?C | 30.5.2799
SUF2INV23 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F2 INV23 | TmpStk3_Pcb_F | ?C | 30.5.2800
SUF2INV23 | 106 | MV transformer pressure | SU F2 INV23 | PresTrf_F | "-" | 30.5.2801
SUF2INV23 | 110 | Switching status of the DC load-break switch | SU F2 INV23 | DcSwStt | "-" | 30.5.2802
SUINV23JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV23 | Dat_UpdCnt_1 | "-" | 30.5.2803
SUINV23JB1 | 2 | DC current input 1 | SU F2 INV23 | DcMs_Amp_01 | A | 30.5.2804
SUINV23JB1 | 3 | DC current input 2 | SU F2 INV23 | DcMs_Amp_02 | A | 30.5.2805
SUINV23JB1 | 4 | DC current input 3 | SU F2 INV23 | DcMs_Amp_03 | A | 30.5.2806
SUINV23JB1 | 5 | DC current input 4 | SU F2 INV23 | DcMs_Amp_04 | A | 30.5.2807
SUINV23JB1 | 6 | DC current input 5 | SU F2 INV23 | DcMs_Amp_05 | A | 30.5.2808
SUINV23JB1 | 7 | DC current input 6 | SU F2 INV23 | DcMs_Amp_06 | A | 30.5.2809
SUINV23JB1 | 8 | DC current input 7 | SU F2 INV23 | DcMs_Amp_07 | A | 30.5.2810
SUINV23JB1 | 9 | DC current input 8 | SU F2 INV23 | DcMs_Amp_08 | A | 30.5.2811
SUINV23JB1 | 10 | DC current input 9 | SU F2 INV23 | DcMs_Amp_09 | A | 30.5.2812
SUINV23JB1 | 11 | DC current input 10 | SU F2 INV23 | DcMs_Amp_10 | A | 30.5.2813
SUINV23JB1 | 12 | DC current input 11 | SU F2 INV23 | DcMs_Amp_11 | A | 30.5.2814
SUINV23JB1 | 13 | DC current input 12 | SU F2 INV23 | DcMs_Amp_12 | A | 30.5.2815
SUINV23JB1 | 14 | DC current input 13 | SU F2 INV23 | DcMs_Amp_13 | A | 30.5.2816
SUINV23JB1 | 15 | DC current input 14 | SU F2 INV23 | DcMs_Amp_14 | A | 30.5.2817
SUINV23JB1 | 16 | DC current input 15 | SU F2 INV23 | DcMs_Amp_15 | A | 30.5.2818
SUINV23JB1 | 17 | DC current input 16 | SU F2 INV23 | DcMs_Amp_16 | A | 30.5.2819
SUINV23JB1 | 18 | DC current input 1 | SU F2 INV23 | DcMs_Amp_01_F | A | 30.5.2820
SUINV23JB1 | 19 | DC current input 2 | SU F2 INV23 | DcMs_Amp_02_F | A | 30.5.2821
SUINV23JB1 | 20 | DC current input 3 | SU F2 INV23 | DcMs_Amp_03_F | A | 30.5.2822
SUINV23JB1 | 21 | DC current input 4 | SU F2 INV23 | DcMs_Amp_04_F | A | 30.5.2823
SUINV23JB1 | 22 | DC current input 5 | SU F2 INV23 | DcMs_Amp_05_F | A | 30.5.2824
SUINV23JB1 | 23 | DC current input 6 | SU F2 INV23 | DcMs_Amp_06_F | A | 30.5.2825
SUINV23JB1 | 24 | DC current input 7 | SU F2 INV23 | DcMs_Amp_07_F | A | 30.5.2826
SUINV23JB1 | 25 | DC current input 8 | SU F2 INV23 | DcMs_Amp_08_F | A | 30.5.2827
SUINV23JB1 | 26 | DC current input 9 | SU F2 INV23 | DcMs_Amp_09_F | A | 30.5.2828
SUINV23JB1 | 27 | DC current input 10 | SU F2 INV23 | DcMs_Amp_10_F | A | 30.5.2829
SUINV23JB1 | 28 | DC current input 11 | SU F2 INV23 | DcMs_Amp_11_F | A | 30.5.2830
SUINV23JB1 | 29 | DC current input 12 | SU F2 INV23 | DcMs_Amp_12_F | A | 30.5.2831
SUINV23JB1 | 30 | DC current input 13 | SU F2 INV23 | DcMs_Amp_13_F | A | 30.5.2832
SUINV23JB1 | 31 | DC current input 14 | SU F2 INV23 | DcMs_Amp_14_F | A | 30.5.2833
SUINV23JB1 | 32 | DC current input 15 | SU F2 INV23 | DcMs_Amp_15_F | A | 30.5.2834
SUINV23JB1 | 33 | DC current input 16 | SU F2 INV23 | DcMs_Amp_16_F | A | 30.5.2835
SUINV23JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F2 INV23 | Dat_UpdCnt_1 | "-" | 30.5.2836
SUINV23JB2 | 2 | DC current input 1 | SU F2 INV23 | DcMs_Amp_01 | A | 30.5.2837
SUINV23JB2 | 3 | DC current input 2 | SU F2 INV23 | DcMs_Amp_02 | A | 30.5.2838
SUINV23JB2 | 4 | DC current input 3 | SU F2 INV23 | DcMs_Amp_03 | A | 30.5.2839
SUINV23JB2 | 5 | DC current input 4 | SU F2 INV23 | DcMs_Amp_04 | A | 30.5.2840
SUINV23JB2 | 6 | DC current input 5 | SU F2 INV23 | DcMs_Amp_05 | A | 30.5.2841
SUINV23JB2 | 7 | DC current input 6 | SU F2 INV23 | DcMs_Amp_06 | A | 30.5.2842
SUINV23JB2 | 8 | DC current input 7 | SU F2 INV23 | DcMs_Amp_07 | A | 30.5.2843
SUINV23JB2 | 9 | DC current input 8 | SU F2 INV23 | DcMs_Amp_08 | A | 30.5.2844
SUINV23JB2 | 10 | DC current input 9 | SU F2 INV23 | DcMs_Amp_09 | A | 30.5.2845
SUINV23JB2 | 11 | DC current input 10 | SU F2 INV23 | DcMs_Amp_10 | A | 30.5.2846
SUINV23JB2 | 12 | DC current input 11 | SU F2 INV23 | DcMs_Amp_11 | A | 30.5.2847
SUINV23JB2 | 13 | DC current input 12 | SU F2 INV23 | DcMs_Amp_12 | A | 30.5.2848
SUINV23JB2 | 14 | DC current input 13 | SU F2 INV23 | DcMs_Amp_13 | A | 30.5.2849
SUINV23JB2 | 15 | DC current input 14 | SU F2 INV23 | DcMs_Amp_14 | A | 30.5.2850
SUINV23JB2 | 16 | DC current input 15 | SU F2 INV23 | DcMs_Amp_15 | A | 30.5.2851
SUINV23JB2 | 17 | DC current input 16 | SU F2 INV23 | DcMs_Amp_16 | A | 30.5.2852
SUINV23JB2 | 18 | DC current input 1 | SU F2 INV23 | DcMs_Amp_01_F | A | 30.5.2853
SUINV23JB2 | 19 | DC current input 2 | SU F2 INV23 | DcMs_Amp_02_F | A | 30.5.2854
SUINV23JB2 | 20 | DC current input 3 | SU F2 INV23 | DcMs_Amp_03_F | A | 30.5.2855
SUINV23JB2 | 21 | DC current input 4 | SU F2 INV23 | DcMs_Amp_04_F | A | 30.5.2856
SUINV23JB2 | 22 | DC current input 5 | SU F2 INV23 | DcMs_Amp_05_F | A | 30.5.2857
SUINV23JB2 | 23 | DC current input 6 | SU F2 INV23 | DcMs_Amp_06_F | A | 30.5.2858
SUINV23JB2 | 24 | DC current input 7 | SU F2 INV23 | DcMs_Amp_07_F | A | 30.5.2859
SUINV23JB2 | 25 | DC current input 8 | SU F2 INV23 | DcMs_Amp_08_F | A | 30.5.2860
SUINV23JB2 | 26 | DC current input 9 | SU F2 INV23 | DcMs_Amp_09_F | A | 30.5.2861
SUINV23JB2 | 27 | DC current input 10 | SU F2 INV23 | DcMs_Amp_10_F | A | 30.5.2862
SUINV23JB2 | 28 | DC current input 11 | SU F2 INV23 | DcMs_Amp_11_F | A | 30.5.2863
SUINV23JB2 | 29 | DC current input 12 | SU F2 INV23 | DcMs_Amp_12_F | A | 30.5.2864
SUINV23JB2 | 30 | DC current input 13 | SU F2 INV23 | DcMs_Amp_13_F | A | 30.5.2865
SUINV23JB2 | 31 | DC current input 14 | SU F2 INV23 | DcMs_Amp_14_F | A | 30.5.2866
SUINV23JB2 | 32 | DC current input 15 | SU F2 INV23 | DcMs_Amp_15_F | A | 30.5.2867
SUINV23JB2 | 33 | DC current input 16 | SU F2 INV23 | DcMs_Amp_16_F | A | 30.5.2868
SUF352F3 | 15 |  | SU F3 52F3 | Breaker device control block | Blocking | 30.5.2869
SUF352F3 | 18 |  | SU F3 52F3 | Cause of interlocking | Cause | 30.5.2870
SUF352F3 | 19 |  | SU F3 52F3 | Breaker selection on monitor | Sessions | 30.5.2871
SUF352F3 | 55 |  | SU F3 52F3 | Add cause of command | Add Cause | 30.5.2872
SUF352I | 131 |  | SU F3 52M | Current | A | 30.5.2873
SUF352P | 133 |  | SU F3 52M | Active Power | MW | 30.5.2874
SUF352PF | 136 |  | SU F3 52M | Power Factor | Cosfii | 30.5.2875
SUF352Q | 134 |  | SU F3 52M | Reactive Power | Mvar | 30.5.2876
SUF352V | 132 |  | SU F3 52M | Voltage | kV | 30.5.2877
SUF3 | 20 |  | SU F3 BAY | Bay blockings | Blocking | 30.5.2878
SUF3 | 21 |  | SU F3 BAY | Bay selection on monitor | Sessions | 30.5.2879
SUF3INV10 | 1 | DC voltage DC plus to DC minus | SU F3 INV10 | DcMs_Vol | V | 30.5.2880
SUF3INV10 | 2 | DC current inverter bridge 1 | SU F3 INV10 | DcMs_Amp_Stk1 | A | 30.5.2881
SUF3INV10 | 3 | DC current inverter bridge 2 | SU F3 INV10 | DcMs_Amp_Stk2 | A | 30.5.2882
SUF3INV10 | 4 | DC current inverter bridge 3 | SU F3 INV10 | DcMs_Amp_Stk3 | A | 30.5.2883
SUF3INV10 | 5 | DC current, total | SU F3 INV10 | DcMs_TotAmp | A | 30.5.2884
SUF3INV10 | 6 | DC power, total | SU F3 INV10 | DcMs_TotWatt | kW | 30.5.2885
SUF3INV10 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV10 | InvMs_DclVol_Stk1 | V | 30.5.2886
SUF3INV10 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV10 | InvMs_DclVol_Stk2 | V | 30.5.2887
SUF3INV10 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV10 | InvMs_DclVol_Stk3 | V | 30.5.2888
SUF3INV10 | 10 | AC current L1, total | SU F3 INV10 | InvMs_TotA_PhsA | A | 30.5.2889
SUF3INV10 | 11 | AC current L2, total | SU F3 INV10 | InvMs_TotA_PhsB | A | 30.5.2890
SUF3INV10 | 12 | AC current L3, total | SU F3 INV10 | InvMs_TotA_PhsC | A | 30.5.2891
SUF3INV10 | 13 | Power factor (cos phi) | SU F3 INV10 | InvMs_PF | "-" | 30.5.2892
SUF3INV10 | 14 | Apparent power, total | SU F3 INV10 | InvMs_TotVA | kVA | 30.5.2893
SUF3INV10 | 15 | Active power, total | SU F3 INV10 | InvMs_TotW | kW | 30.5.2894
SUF3INV10 | 16 | Reactive power, total | SU F3 INV10 | InvMs_TotVAr | kVAr | 30.5.2895
SUF3INV10 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV10 | GriMs_V_PhsAB | V | 30.5.2896
SUF3INV10 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV10 | GriMs_V_PhsBC | V | 30.5.2897
SUF3INV10 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV10 | GriMs_V_PhsCA | V | 30.5.2898
SUF3INV10 | 20 | Power frequency | SU F3 INV10 | GriMs_Hz | Hz | 30.5.2899
SUF3INV10 | 21 | Temperature in the AC range | SU F3 INV10 | TmpCab_Acc | °C | 30.5.2900
SUF3INV10 | 22 | Temperature in the DC range | SU F3 INV10 | TmpCab_Dcc | °C | 30.5.2901
SUF3INV10 | 23 | Temperature in the electronics area | SU F3 INV10 | TmpCab_Rio | °C | 30.5.2902
SUF3INV10 | 24 | Temperature in interior, maximum value | SU F3 INV10 | TmpCab_Max | °C | 30.5.2903
SUF3INV10 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV10 | TmpStk_IgbtMax | °C | 30.5.2904
SUF3INV10 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV10 | TmpStk_PcbMax | °C | 30.5.2905
SUF3INV10 | 27 | Outside temperature | SU F3 INV10 | TmpExl | ?C | 30.5.2906
SUF3INV10 | 28 | Temperature of the MV transformer | SU F3 INV10 | TmpTrf | °C | 30.5.2907
SUF3INV10 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV10 | DcSw1Stt | "-" | 30.5.2908
SUF3INV10 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV10 | DcSw2Stt | "-" | 30.5.2909
SUF3INV10 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV10 | DcSw3Stt | "-" | 30.5.2910
SUF3INV10 | 32 | Switching status of the AC circuit breaker | SU F3 INV10 | AcSwStt | "-" | 30.5.2911
SUF3INV10 | 33 | Switching state of the capacitor contactor | SU F3 INV10 | CapacSwStt | "-" | 30.5.2912
SUF3INV10 | 34 | Switching status of the pre-charging contactor | SU F3 INV10 | PrchrgSwStt | "-" | 30.5.2913
SUF3INV10 | 35 | Feed-in hours | SU F3 INV10 | Cnt_TotFeedTm | "-" | 30.5.2914
SUF3INV10 | 36 | Operating hours | SU F3 INV10 | Cnt_TotOpTm | "-" | 30.5.2915
SUF3INV10 | 37 | DC energy drawn, total | SU F3 INV10 | Cnt_TotWatthIn | MWh | 30.5.2916
SUF3INV10 | 38 | AC energy fed in, total | SU F3 INV10 | Cnt_TotWhOut | MWh | 30.5.2917
SUF3INV10 | 39 | DC energy drawn that day | SU F3 INV10 | Cnt_WatthIn | MWh | 30.5.2918
SUF3INV10 | 40 | AC energy fed in that day | SU F3 INV10 | Cnt_WhOut | MWh | 30.5.2919
SUF3INV10 | 41 | Operating hours of the interior fan 1 | SU F3 INV10 | Cnt_FanCab1Tm | "-" | 30.5.2920
SUF3INV10 | 42 | Operating hours of the interior fan 2 | SU F3 INV10 | Cnt_FanCab2Tm | "-" | 30.5.2921
SUF3INV10 | 43 | Operating hours of the inverter bridge fan | SU F3 INV10 | Cnt_FanStkTm | "-" | 30.5.2922
SUF3INV10 | 44 | Operating hours of the internal heating element | SU F3 INV10 | Cnt_HtCabTm | "-" | 30.5.2923
SUF3INV10 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV10 | Cnt_HtLoExlTmpTm | "-" | 30.5.2924
SUF3INV10 | 46 | Error location of the present error | SU F3 INV10 | ErrLcn | "-" | 30.5.2925
SUF3INV10 | 47 | Error status of the inverter | SU F3 INV10 | ErrStt | "-" | 30.5.2926
SUF3INV10 | 48 | Error number of the present error | SU F3 INV10 | ErrNo | "-" | 30.5.2927
SUF3INV10 | 49 | Operating state of the inverter | SU F3 INV10 | OpStt | "-" | 30.5.2928
SUF3INV10 | 50 | Switch status of the start-stop key switch | SU F3 INV10 | Rio_KeySw | "-" | 30.5.2929
SUF3INV10 | 51 | Waiting time for grid connection | SU F3 INV10 | WaitGriTm | s | 30.5.2930
SUF3INV10 | 52 | Inverter serial number | SU F3 INV10 | DevInf_SerNo | "-" | 30.5.2931
SUF3INV10 | 53 | Switching status of the GFDI | SU F3 INV10 | GfdiSwStt | "-" | 30.5.2932
SUF3INV10 | 54 | Active power, setpoint | SU F3 INV10 | WSpt | kW | 30.5.2933
SUF3INV10 | 55 | Maximum apparent power, setpoint | SU F3 INV10 | VAMaxSpt | kVA | 30.5.2934
SUF3INV10 | 56 | Reactive power, setpoint | SU F3 INV10 | VArSpt | kVAr | 30.5.2935
SUF3INV10 | 57 | Power factor cos (phi), setpoint | SU F3 INV10 | PFSpt | "-" | 30.5.2936
SUF3INV10 | 58 | Fast stop hermetic protection, pressure | SU F3 INV10 | TrfPro_Pres | "-" | 30.5.2937
SUF3INV10 | 59 | Fast stop hermetic protection, temperature | SU F3 INV10 | TrfPro_TmpTrp | "-" | 30.5.2938
SUF3INV10 | 60 | Hermetic protection, gas fill level | SU F3 INV10 | TrfPro_GasOilLev | "-" | 30.5.2939
SUF3INV10 | 61 | Hermetic pressure, temperature warning | SU F3 INV10 | TrfPro_TmpWrn | "-" | 30.5.2940
SUF3INV10 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV10 | TmpStk1_Igbt | °C | 30.5.2941
SUF3INV10 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV10 | TmpStk2_Igbt | °C | 30.5.2942
SUF3INV10 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV10 | TmpStk3_Igbt | °C | 30.5.2943
SUF3INV10 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV10 | TmpStk1_Pcb | ?C | 30.5.2944
SUF3INV10 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV10 | TmpStk2_Pcb | ?C | 30.5.2945
SUF3INV10 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV10 | TmpStk3_Pcb | ?C | 30.5.2946
SUF3INV10 | 68 | AC Energy Fed in the previous Day | SU F3 INV10 | Cnt_YstdWhOut | MWh | 30.5.2947
SUF3INV10 | 69 | CPU running time since system start | SU F3 INV10 | Cpu1UpTime | s | 30.5.2948
SUF3INV10 | 70 | Insulation resistance | SU F3 INV10 | PvGnd_RisIso | kOhm | 30.5.2949
SUF3INV10 | 71 | MV transformer pressure | SU F3 INV10 | PresTrf | "-" | 30.5.2950
SUF3INV10 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV10 | PresTrf_ErrStt | "-" | 30.5.2951
SUF3INV10 | 73 | DC voltage DC plus to DC minus | SU F3 INV10 | DcMs_Vol_F | V | 30.5.2952
SUF3INV10 | 74 | DC current inverter bridge 1 | SU F3 INV10 | DcMs_Amp_Stk1_F | A | 30.5.2953
SUF3INV10 | 75 | DC current inverter bridge 2 | SU F3 INV10 | DcMs_Amp_Stk2_F | A | 30.5.2954
SUF3INV10 | 76 | DC current inverter bridge 3 | SU F3 INV10 | DcMs_Amp_Stk3_F | A | 30.5.2955
SUF3INV10 | 77 | DC current, total | SU F3 INV10 | DcMs_TotAmp_F | A | 30.5.2956
SUF3INV10 | 78 | DC power, total | SU F3 INV10 | DcMs_TotWatt_F | kW | 30.5.2957
SUF3INV10 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV10 | InvMs_DclVol_Stk1_F | V | 30.5.2958
SUF3INV10 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV10 | InvMs_DclVol_Stk2_F | V | 30.5.2959
SUF3INV10 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV10 | InvMs_DclVol_Stk3_F | V | 30.5.2960
SUF3INV10 | 82 | AC current L1, total | SU F3 INV10 | InvMs_TotA_PhsA_F | A | 30.5.2961
SUF3INV10 | 83 | AC current L2, total | SU F3 INV10 | InvMs_TotA_PhsB_F | A | 30.5.2962
SUF3INV10 | 84 | AC current L3, total | SU F3 INV10 | InvMs_TotA_PhsC_F | A | 30.5.2963
SUF3INV10 | 85 | Power factor (cos phi) | SU F3 INV10 | InvMs_PF_F | "-" | 30.5.2964
SUF3INV10 | 86 | Active power, total | SU F3 INV10 | InvMs_TotW_F | kW | 30.5.2965
SUF3INV10 | 87 | Reactive power, total | SU F3 INV10 | InvMs_TotVAr_F | kVAr | 30.5.2966
SUF3INV10 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV10 | GriMs_V_PhsAB_F | V | 30.5.2967
SUF3INV10 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV10 | GriMs_V_PhsBC_F | V | 30.5.2968
SUF3INV10 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV10 | GriMs_V_PhsCA_F | V | 30.5.2969
SUF3INV10 | 91 | Power frequency | SU F3 INV10 | GriMs_Hz_F | Hz | 30.5.2970
SUF3INV10 | 92 | Temperature in the AC range | SU F3 INV10 | TmpCab_Acc_F | °C | 30.5.2971
SUF3INV10 | 93 | Temperature in the DC range | SU F3 INV10 | TmpCab_Dcc_F | °C | 30.5.2972
SUF3INV10 | 94 | Temperature in the electronics area | SU F3 INV10 | TmpCab_Rio_F | °C | 30.5.2973
SUF3INV10 | 95 | Temperature in interior, maximum value | SU F3 INV10 | TmpCab_Max_F | °C | 30.5.2974
SUF3INV10 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV10 | TmpStk_IgbtMax_F | °C | 30.5.2975
SUF3INV10 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV10 | TmpStk_PcbMax_F | °C | 30.5.2976
SUF3INV10 | 98 | Outside temperature | SU F3 INV10 | TmpExl_F | ?C | 30.5.2977
SUF3INV10 | 99 | Temperature of the MV transformer | SU F3 INV10 | TmpTrf_F | °C | 30.5.2978
SUF3INV10 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV10 | TmpStk1_Igbt_F | °C | 30.5.2979
SUF3INV10 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV10 | TmpStk2_Igbt_F | °C | 30.5.2980
SUF3INV10 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV10 | TmpStk3_Igbt_F | °C | 30.5.2981
SUF3INV10 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV10 | TmpStk1_Pcb_F | ?C | 30.5.2982
SUF3INV10 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV10 | TmpStk2_Pcb_F | ?C | 30.5.2983
SUF3INV10 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV10 | TmpStk3_Pcb_F | ?C | 30.5.2984
SUF3INV10 | 106 | MV transformer pressure | SU F3 INV10 | PresTrf_F | "-" | 30.5.2985
SUF3INV10 | 110 | Switching status of the DC load-break switch | SU F3 INV10 | DcSwStt | "-" | 30.5.2986
SUINV10JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV10 | Dat_UpdCnt_1 | "-" | 30.5.2987
SUINV10JB1 | 2 | DC current input 1 | SU F3 INV10 | DcMs_Amp_01 | A | 30.5.2988
SUINV10JB1 | 3 | DC current input 2 | SU F3 INV10 | DcMs_Amp_02 | A | 30.5.2989
SUINV10JB1 | 4 | DC current input 3 | SU F3 INV10 | DcMs_Amp_03 | A | 30.5.2990
SUINV10JB1 | 5 | DC current input 4 | SU F3 INV10 | DcMs_Amp_04 | A | 30.5.2991
SUINV10JB1 | 6 | DC current input 5 | SU F3 INV10 | DcMs_Amp_05 | A | 30.5.2992
SUINV10JB1 | 7 | DC current input 6 | SU F3 INV10 | DcMs_Amp_06 | A | 30.5.2993
SUINV10JB1 | 8 | DC current input 7 | SU F3 INV10 | DcMs_Amp_07 | A | 30.5.2994
SUINV10JB1 | 9 | DC current input 8 | SU F3 INV10 | DcMs_Amp_08 | A | 30.5.2995
SUINV10JB1 | 10 | DC current input 9 | SU F3 INV10 | DcMs_Amp_09 | A | 30.5.2996
SUINV10JB1 | 11 | DC current input 10 | SU F3 INV10 | DcMs_Amp_10 | A | 30.5.2997
SUINV10JB1 | 12 | DC current input 11 | SU F3 INV10 | DcMs_Amp_11 | A | 30.5.2998
SUINV10JB1 | 13 | DC current input 12 | SU F3 INV10 | DcMs_Amp_12 | A | 30.5.2999
SUINV10JB1 | 14 | DC current input 13 | SU F3 INV10 | DcMs_Amp_13 | A | 30.5.3000
SUINV10JB1 | 15 | DC current input 14 | SU F3 INV10 | DcMs_Amp_14 | A | 30.5.3001
SUINV10JB1 | 16 | DC current input 15 | SU F3 INV10 | DcMs_Amp_15 | A | 30.5.3002
SUINV10JB1 | 17 | DC current input 16 | SU F3 INV10 | DcMs_Amp_16 | A | 30.5.3003
SUINV10JB1 | 18 | DC current input 1 | SU F3 INV10 | DcMs_Amp_01_F | A | 30.5.3004
SUINV10JB1 | 19 | DC current input 2 | SU F3 INV10 | DcMs_Amp_02_F | A | 30.5.3005
SUINV10JB1 | 20 | DC current input 3 | SU F3 INV10 | DcMs_Amp_03_F | A | 30.5.3006
SUINV10JB1 | 21 | DC current input 4 | SU F3 INV10 | DcMs_Amp_04_F | A | 30.5.3007
SUINV10JB1 | 22 | DC current input 5 | SU F3 INV10 | DcMs_Amp_05_F | A | 30.5.3008
SUINV10JB1 | 23 | DC current input 6 | SU F3 INV10 | DcMs_Amp_06_F | A | 30.5.3009
SUINV10JB1 | 24 | DC current input 7 | SU F3 INV10 | DcMs_Amp_07_F | A | 30.5.3010
SUINV10JB1 | 25 | DC current input 8 | SU F3 INV10 | DcMs_Amp_08_F | A | 30.5.3011
SUINV10JB1 | 26 | DC current input 9 | SU F3 INV10 | DcMs_Amp_09_F | A | 30.5.3012
SUINV10JB1 | 27 | DC current input 10 | SU F3 INV10 | DcMs_Amp_10_F | A | 30.5.3013
SUINV10JB1 | 28 | DC current input 11 | SU F3 INV10 | DcMs_Amp_11_F | A | 30.5.3014
SUINV10JB1 | 29 | DC current input 12 | SU F3 INV10 | DcMs_Amp_12_F | A | 30.5.3015
SUINV10JB1 | 30 | DC current input 13 | SU F3 INV10 | DcMs_Amp_13_F | A | 30.5.3016
SUINV10JB1 | 31 | DC current input 14 | SU F3 INV10 | DcMs_Amp_14_F | A | 30.5.3017
SUINV10JB1 | 32 | DC current input 15 | SU F3 INV10 | DcMs_Amp_15_F | A | 30.5.3018
SUINV10JB1 | 33 | DC current input 16 | SU F3 INV10 | DcMs_Amp_16_F | A | 30.5.3019
SUINV10JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV10 | Dat_UpdCnt_1 | "-" | 30.5.3020
SUINV10JB2 | 2 | DC current input 1 | SU F3 INV10 | DcMs_Amp_01 | A | 30.5.3021
SUINV10JB2 | 3 | DC current input 2 | SU F3 INV10 | DcMs_Amp_02 | A | 30.5.3022
SUINV10JB2 | 4 | DC current input 3 | SU F3 INV10 | DcMs_Amp_03 | A | 30.5.3023
SUINV10JB2 | 5 | DC current input 4 | SU F3 INV10 | DcMs_Amp_04 | A | 30.5.3024
SUINV10JB2 | 6 | DC current input 5 | SU F3 INV10 | DcMs_Amp_05 | A | 30.5.3025
SUINV10JB2 | 7 | DC current input 6 | SU F3 INV10 | DcMs_Amp_06 | A | 30.5.3026
SUINV10JB2 | 8 | DC current input 7 | SU F3 INV10 | DcMs_Amp_07 | A | 30.5.3027
SUINV10JB2 | 9 | DC current input 8 | SU F3 INV10 | DcMs_Amp_08 | A | 30.5.3028
SUINV10JB2 | 10 | DC current input 9 | SU F3 INV10 | DcMs_Amp_09 | A | 30.5.3029
SUINV10JB2 | 11 | DC current input 10 | SU F3 INV10 | DcMs_Amp_10 | A | 30.5.3030
SUINV10JB2 | 12 | DC current input 11 | SU F3 INV10 | DcMs_Amp_11 | A | 30.5.3031
SUINV10JB2 | 13 | DC current input 12 | SU F3 INV10 | DcMs_Amp_12 | A | 30.5.3032
SUINV10JB2 | 14 | DC current input 13 | SU F3 INV10 | DcMs_Amp_13 | A | 30.5.3033
SUINV10JB2 | 15 | DC current input 14 | SU F3 INV10 | DcMs_Amp_14 | A | 30.5.3034
SUINV10JB2 | 16 | DC current input 15 | SU F3 INV10 | DcMs_Amp_15 | A | 30.5.3035
SUINV10JB2 | 17 | DC current input 16 | SU F3 INV10 | DcMs_Amp_16 | A | 30.5.3036
SUINV10JB2 | 18 | DC current input 1 | SU F3 INV10 | DcMs_Amp_01_F | A | 30.5.3037
SUINV10JB2 | 19 | DC current input 2 | SU F3 INV10 | DcMs_Amp_02_F | A | 30.5.3038
SUINV10JB2 | 20 | DC current input 3 | SU F3 INV10 | DcMs_Amp_03_F | A | 30.5.3039
SUINV10JB2 | 21 | DC current input 4 | SU F3 INV10 | DcMs_Amp_04_F | A | 30.5.3040
SUINV10JB2 | 22 | DC current input 5 | SU F3 INV10 | DcMs_Amp_05_F | A | 30.5.3041
SUINV10JB2 | 23 | DC current input 6 | SU F3 INV10 | DcMs_Amp_06_F | A | 30.5.3042
SUINV10JB2 | 24 | DC current input 7 | SU F3 INV10 | DcMs_Amp_07_F | A | 30.5.3043
SUINV10JB2 | 25 | DC current input 8 | SU F3 INV10 | DcMs_Amp_08_F | A | 30.5.3044
SUINV10JB2 | 26 | DC current input 9 | SU F3 INV10 | DcMs_Amp_09_F | A | 30.5.3045
SUINV10JB2 | 27 | DC current input 10 | SU F3 INV10 | DcMs_Amp_10_F | A | 30.5.3046
SUINV10JB2 | 28 | DC current input 11 | SU F3 INV10 | DcMs_Amp_11_F | A | 30.5.3047
SUINV10JB2 | 29 | DC current input 12 | SU F3 INV10 | DcMs_Amp_12_F | A | 30.5.3048
SUINV10JB2 | 30 | DC current input 13 | SU F3 INV10 | DcMs_Amp_13_F | A | 30.5.3049
SUINV10JB2 | 31 | DC current input 14 | SU F3 INV10 | DcMs_Amp_14_F | A | 30.5.3050
SUINV10JB2 | 32 | DC current input 15 | SU F3 INV10 | DcMs_Amp_15_F | A | 30.5.3051
SUINV10JB2 | 33 | DC current input 16 | SU F3 INV10 | DcMs_Amp_16_F | A | 30.5.3052
SUF3INV11 | 1 | DC voltage DC plus to DC minus | SU F3 INV11 | DcMs_Vol | V | 30.5.3053
SUF3INV11 | 2 | DC current inverter bridge 1 | SU F3 INV11 | DcMs_Amp_Stk1 | A | 30.5.3054
SUF3INV11 | 3 | DC current inverter bridge 2 | SU F3 INV11 | DcMs_Amp_Stk2 | A | 30.5.3055
SUF3INV11 | 4 | DC current inverter bridge 3 | SU F3 INV11 | DcMs_Amp_Stk3 | A | 30.5.3056
SUF3INV11 | 5 | DC current, total | SU F3 INV11 | DcMs_TotAmp | A | 30.5.3057
SUF3INV11 | 6 | DC power, total | SU F3 INV11 | DcMs_TotWatt | kW | 30.5.3058
SUF3INV11 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV11 | InvMs_DclVol_Stk1 | V | 30.5.3059
SUF3INV11 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV11 | InvMs_DclVol_Stk2 | V | 30.5.3060
SUF3INV11 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV11 | InvMs_DclVol_Stk3 | V | 30.5.3061
SUF3INV11 | 10 | AC current L1, total | SU F3 INV11 | InvMs_TotA_PhsA | A | 30.5.3062
SUF3INV11 | 11 | AC current L2, total | SU F3 INV11 | InvMs_TotA_PhsB | A | 30.5.3063
SUF3INV11 | 12 | AC current L3, total | SU F3 INV11 | InvMs_TotA_PhsC | A | 30.5.3064
SUF3INV11 | 13 | Power factor (cos phi) | SU F3 INV11 | InvMs_PF | "-" | 30.5.3065
SUF3INV11 | 14 | Apparent power, total | SU F3 INV11 | InvMs_TotVA | kVA | 30.5.3066
SUF3INV11 | 15 | Active power, total | SU F3 INV11 | InvMs_TotW | kW | 30.5.3067
SUF3INV11 | 16 | Reactive power, total | SU F3 INV11 | InvMs_TotVAr | kVAr | 30.5.3068
SUF3INV11 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV11 | GriMs_V_PhsAB | V | 30.5.3069
SUF3INV11 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV11 | GriMs_V_PhsBC | V | 30.5.3070
SUF3INV11 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV11 | GriMs_V_PhsCA | V | 30.5.3071
SUF3INV11 | 20 | Power frequency | SU F3 INV11 | GriMs_Hz | Hz | 30.5.3072
SUF3INV11 | 21 | Temperature in the AC range | SU F3 INV11 | TmpCab_Acc | °C | 30.5.3073
SUF3INV11 | 22 | Temperature in the DC range | SU F3 INV11 | TmpCab_Dcc | °C | 30.5.3074
SUF3INV11 | 23 | Temperature in the electronics area | SU F3 INV11 | TmpCab_Rio | °C | 30.5.3075
SUF3INV11 | 24 | Temperature in interior, maximum value | SU F3 INV11 | TmpCab_Max | °C | 30.5.3076
SUF3INV11 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV11 | TmpStk_IgbtMax | °C | 30.5.3077
SUF3INV11 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV11 | TmpStk_PcbMax | °C | 30.5.3078
SUF3INV11 | 27 | Outside temperature | SU F3 INV11 | TmpExl | ?C | 30.5.3079
SUF3INV11 | 28 | Temperature of the MV transformer | SU F3 INV11 | TmpTrf | °C | 30.5.3080
SUF3INV11 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV11 | DcSw1Stt | "-" | 30.5.3081
SUF3INV11 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV11 | DcSw2Stt | "-" | 30.5.3082
SUF3INV11 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV11 | DcSw3Stt | "-" | 30.5.3083
SUF3INV11 | 32 | Switching status of the AC circuit breaker | SU F3 INV11 | AcSwStt | "-" | 30.5.3084
SUF3INV11 | 33 | Switching state of the capacitor contactor | SU F3 INV11 | CapacSwStt | "-" | 30.5.3085
SUF3INV11 | 34 | Switching status of the pre-charging contactor | SU F3 INV11 | PrchrgSwStt | "-" | 30.5.3086
SUF3INV11 | 35 | Feed-in hours | SU F3 INV11 | Cnt_TotFeedTm | "-" | 30.5.3087
SUF3INV11 | 36 | Operating hours | SU F3 INV11 | Cnt_TotOpTm | "-" | 30.5.3088
SUF3INV11 | 37 | DC energy drawn, total | SU F3 INV11 | Cnt_TotWatthIn | MWh | 30.5.3089
SUF3INV11 | 38 | AC energy fed in, total | SU F3 INV11 | Cnt_TotWhOut | MWh | 30.5.3090
SUF3INV11 | 39 | DC energy drawn that day | SU F3 INV11 | Cnt_WatthIn | MWh | 30.5.3091
SUF3INV11 | 40 | AC energy fed in that day | SU F3 INV11 | Cnt_WhOut | MWh | 30.5.3092
SUF3INV11 | 41 | Operating hours of the interior fan 1 | SU F3 INV11 | Cnt_FanCab1Tm | "-" | 30.5.3093
SUF3INV11 | 42 | Operating hours of the interior fan 2 | SU F3 INV11 | Cnt_FanCab2Tm | "-" | 30.5.3094
SUF3INV11 | 43 | Operating hours of the inverter bridge fan | SU F3 INV11 | Cnt_FanStkTm | "-" | 30.5.3095
SUF3INV11 | 44 | Operating hours of the internal heating element | SU F3 INV11 | Cnt_HtCabTm | "-" | 30.5.3096
SUF3INV11 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV11 | Cnt_HtLoExlTmpTm | "-" | 30.5.3097
SUF3INV11 | 46 | Error location of the present error | SU F3 INV11 | ErrLcn | "-" | 30.5.3098
SUF3INV11 | 47 | Error status of the inverter | SU F3 INV11 | ErrStt | "-" | 30.5.3099
SUF3INV11 | 48 | Error number of the present error | SU F3 INV11 | ErrNo | "-" | 30.5.3100
SUF3INV11 | 49 | Operating state of the inverter | SU F3 INV11 | OpStt | "-" | 30.5.3101
SUF3INV11 | 50 | Switch status of the start-stop key switch | SU F3 INV11 | Rio_KeySw | "-" | 30.5.3102
SUF3INV11 | 51 | Waiting time for grid connection | SU F3 INV11 | WaitGriTm | s | 30.5.3103
SUF3INV11 | 52 | Inverter serial number | SU F3 INV11 | DevInf_SerNo | "-" | 30.5.3104
SUF3INV11 | 53 | Switching status of the GFDI | SU F3 INV11 | GfdiSwStt | "-" | 30.5.3105
SUF3INV11 | 54 | Active power, setpoint | SU F3 INV11 | WSpt | kW | 30.5.3106
SUF3INV11 | 55 | Maximum apparent power, setpoint | SU F3 INV11 | VAMaxSpt | kVA | 30.5.3107
SUF3INV11 | 56 | Reactive power, setpoint | SU F3 INV11 | VArSpt | kVAr | 30.5.3108
SUF3INV11 | 57 | Power factor cos (phi), setpoint | SU F3 INV11 | PFSpt | "-" | 30.5.3109
SUF3INV11 | 58 | Fast stop hermetic protection, pressure | SU F3 INV11 | TrfPro_Pres | "-" | 30.5.3110
SUF3INV11 | 59 | Fast stop hermetic protection, temperature | SU F3 INV11 | TrfPro_TmpTrp | "-" | 30.5.3111
SUF3INV11 | 60 | Hermetic protection, gas fill level | SU F3 INV11 | TrfPro_GasOilLev | "-" | 30.5.3112
SUF3INV11 | 61 | Hermetic pressure, temperature warning | SU F3 INV11 | TrfPro_TmpWrn | "-" | 30.5.3113
SUF3INV11 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV11 | TmpStk1_Igbt | °C | 30.5.3114
SUF3INV11 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV11 | TmpStk2_Igbt | °C | 30.5.3115
SUF3INV11 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV11 | TmpStk3_Igbt | °C | 30.5.3116
SUF3INV11 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV11 | TmpStk1_Pcb | ?C | 30.5.3117
SUF3INV11 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV11 | TmpStk2_Pcb | ?C | 30.5.3118
SUF3INV11 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV11 | TmpStk3_Pcb | ?C | 30.5.3119
SUF3INV11 | 68 | AC Energy Fed in the previous Day | SU F3 INV11 | Cnt_YstdWhOut | MWh | 30.5.3120
SUF3INV11 | 69 | CPU running time since system start | SU F3 INV11 | Cpu1UpTime | s | 30.5.3121
SUF3INV11 | 70 | Insulation resistance | SU F3 INV11 | PvGnd_RisIso | kOhm | 30.5.3122
SUF3INV11 | 71 | MV transformer pressure | SU F3 INV11 | PresTrf | "-" | 30.5.3123
SUF3INV11 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV11 | PresTrf_ErrStt | "-" | 30.5.3124
SUF3INV11 | 73 | DC voltage DC plus to DC minus | SU F3 INV11 | DcMs_Vol_F | V | 30.5.3125
SUF3INV11 | 74 | DC current inverter bridge 1 | SU F3 INV11 | DcMs_Amp_Stk1_F | A | 30.5.3126
SUF3INV11 | 75 | DC current inverter bridge 2 | SU F3 INV11 | DcMs_Amp_Stk2_F | A | 30.5.3127
SUF3INV11 | 76 | DC current inverter bridge 3 | SU F3 INV11 | DcMs_Amp_Stk3_F | A | 30.5.3128
SUF3INV11 | 77 | DC current, total | SU F3 INV11 | DcMs_TotAmp_F | A | 30.5.3129
SUF3INV11 | 78 | DC power, total | SU F3 INV11 | DcMs_TotWatt_F | kW | 30.5.3130
SUF3INV11 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV11 | InvMs_DclVol_Stk1_F | V | 30.5.3131
SUF3INV11 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV11 | InvMs_DclVol_Stk2_F | V | 30.5.3132
SUF3INV11 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV11 | InvMs_DclVol_Stk3_F | V | 30.5.3133
SUF3INV11 | 82 | AC current L1, total | SU F3 INV11 | InvMs_TotA_PhsA_F | A | 30.5.3134
SUF3INV11 | 83 | AC current L2, total | SU F3 INV11 | InvMs_TotA_PhsB_F | A | 30.5.3135
SUF3INV11 | 84 | AC current L3, total | SU F3 INV11 | InvMs_TotA_PhsC_F | A | 30.5.3136
SUF3INV11 | 85 | Power factor (cos phi) | SU F3 INV11 | InvMs_PF_F | "-" | 30.5.3137
SUF3INV11 | 86 | Active power, total | SU F3 INV11 | InvMs_TotW_F | kW | 30.5.3138
SUF3INV11 | 87 | Reactive power, total | SU F3 INV11 | InvMs_TotVAr_F | kVAr | 30.5.3139
SUF3INV11 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV11 | GriMs_V_PhsAB_F | V | 30.5.3140
SUF3INV11 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV11 | GriMs_V_PhsBC_F | V | 30.5.3141
SUF3INV11 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV11 | GriMs_V_PhsCA_F | V | 30.5.3142
SUF3INV11 | 91 | Power frequency | SU F3 INV11 | GriMs_Hz_F | Hz | 30.5.3143
SUF3INV11 | 92 | Temperature in the AC range | SU F3 INV11 | TmpCab_Acc_F | °C | 30.5.3144
SUF3INV11 | 93 | Temperature in the DC range | SU F3 INV11 | TmpCab_Dcc_F | °C | 30.5.3145
SUF3INV11 | 94 | Temperature in the electronics area | SU F3 INV11 | TmpCab_Rio_F | °C | 30.5.3146
SUF3INV11 | 95 | Temperature in interior, maximum value | SU F3 INV11 | TmpCab_Max_F | °C | 30.5.3147
SUF3INV11 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV11 | TmpStk_IgbtMax_F | °C | 30.5.3148
SUF3INV11 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV11 | TmpStk_PcbMax_F | °C | 30.5.3149
SUF3INV11 | 98 | Outside temperature | SU F3 INV11 | TmpExl_F | ?C | 30.5.3150
SUF3INV11 | 99 | Temperature of the MV transformer | SU F3 INV11 | TmpTrf_F | °C | 30.5.3151
SUF3INV11 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV11 | TmpStk1_Igbt_F | °C | 30.5.3152
SUF3INV11 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV11 | TmpStk2_Igbt_F | °C | 30.5.3153
SUF3INV11 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV11 | TmpStk3_Igbt_F | °C | 30.5.3154
SUF3INV11 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV11 | TmpStk1_Pcb_F | ?C | 30.5.3155
SUF3INV11 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV11 | TmpStk2_Pcb_F | ?C | 30.5.3156
SUF3INV11 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV11 | TmpStk3_Pcb_F | ?C | 30.5.3157
SUF3INV11 | 106 | MV transformer pressure | SU F3 INV11 | PresTrf_F | "-" | 30.5.3158
SUF3INV11 | 110 | Switching status of the DC load-break switch | SU F3 INV11 | DcSwStt | "-" | 30.5.3159
SUINV11JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV11 | Dat_UpdCnt_1 | "-" | 30.5.3160
SUINV11JB1 | 2 | DC current input 1 | SU F3 INV11 | DcMs_Amp_01 | A | 30.5.3161
SUINV11JB1 | 3 | DC current input 2 | SU F3 INV11 | DcMs_Amp_02 | A | 30.5.3162
SUINV11JB1 | 4 | DC current input 3 | SU F3 INV11 | DcMs_Amp_03 | A | 30.5.3163
SUINV11JB1 | 5 | DC current input 4 | SU F3 INV11 | DcMs_Amp_04 | A | 30.5.3164
SUINV11JB1 | 6 | DC current input 5 | SU F3 INV11 | DcMs_Amp_05 | A | 30.5.3165
SUINV11JB1 | 7 | DC current input 6 | SU F3 INV11 | DcMs_Amp_06 | A | 30.5.3166
SUINV11JB1 | 8 | DC current input 7 | SU F3 INV11 | DcMs_Amp_07 | A | 30.5.3167
SUINV11JB1 | 9 | DC current input 8 | SU F3 INV11 | DcMs_Amp_08 | A | 30.5.3168
SUINV11JB1 | 10 | DC current input 9 | SU F3 INV11 | DcMs_Amp_09 | A | 30.5.3169
SUINV11JB1 | 11 | DC current input 10 | SU F3 INV11 | DcMs_Amp_10 | A | 30.5.3170
SUINV11JB1 | 12 | DC current input 11 | SU F3 INV11 | DcMs_Amp_11 | A | 30.5.3171
SUINV11JB1 | 13 | DC current input 12 | SU F3 INV11 | DcMs_Amp_12 | A | 30.5.3172
SUINV11JB1 | 14 | DC current input 13 | SU F3 INV11 | DcMs_Amp_13 | A | 30.5.3173
SUINV11JB1 | 15 | DC current input 14 | SU F3 INV11 | DcMs_Amp_14 | A | 30.5.3174
SUINV11JB1 | 16 | DC current input 15 | SU F3 INV11 | DcMs_Amp_15 | A | 30.5.3175
SUINV11JB1 | 17 | DC current input 16 | SU F3 INV11 | DcMs_Amp_16 | A | 30.5.3176
SUINV11JB1 | 18 | DC current input 1 | SU F3 INV11 | DcMs_Amp_01_F | A | 30.5.3177
SUINV11JB1 | 19 | DC current input 2 | SU F3 INV11 | DcMs_Amp_02_F | A | 30.5.3178
SUINV11JB1 | 20 | DC current input 3 | SU F3 INV11 | DcMs_Amp_03_F | A | 30.5.3179
SUINV11JB1 | 21 | DC current input 4 | SU F3 INV11 | DcMs_Amp_04_F | A | 30.5.3180
SUINV11JB1 | 22 | DC current input 5 | SU F3 INV11 | DcMs_Amp_05_F | A | 30.5.3181
SUINV11JB1 | 23 | DC current input 6 | SU F3 INV11 | DcMs_Amp_06_F | A | 30.5.3182
SUINV11JB1 | 24 | DC current input 7 | SU F3 INV11 | DcMs_Amp_07_F | A | 30.5.3183
SUINV11JB1 | 25 | DC current input 8 | SU F3 INV11 | DcMs_Amp_08_F | A | 30.5.3184
SUINV11JB1 | 26 | DC current input 9 | SU F3 INV11 | DcMs_Amp_09_F | A | 30.5.3185
SUINV11JB1 | 27 | DC current input 10 | SU F3 INV11 | DcMs_Amp_10_F | A | 30.5.3186
SUINV11JB1 | 28 | DC current input 11 | SU F3 INV11 | DcMs_Amp_11_F | A | 30.5.3187
SUINV11JB1 | 29 | DC current input 12 | SU F3 INV11 | DcMs_Amp_12_F | A | 30.5.3188
SUINV11JB1 | 30 | DC current input 13 | SU F3 INV11 | DcMs_Amp_13_F | A | 30.5.3189
SUINV11JB1 | 31 | DC current input 14 | SU F3 INV11 | DcMs_Amp_14_F | A | 30.5.3190
SUINV11JB1 | 32 | DC current input 15 | SU F3 INV11 | DcMs_Amp_15_F | A | 30.5.3191
SUINV11JB1 | 33 | DC current input 16 | SU F3 INV11 | DcMs_Amp_16_F | A | 30.5.3192
SUINV11JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV11 | Dat_UpdCnt_1 | "-" | 30.5.3193
SUINV11JB2 | 2 | DC current input 1 | SU F3 INV11 | DcMs_Amp_01 | A | 30.5.3194
SUINV11JB2 | 3 | DC current input 2 | SU F3 INV11 | DcMs_Amp_02 | A | 30.5.3195
SUINV11JB2 | 4 | DC current input 3 | SU F3 INV11 | DcMs_Amp_03 | A | 30.5.3196
SUINV11JB2 | 5 | DC current input 4 | SU F3 INV11 | DcMs_Amp_04 | A | 30.5.3197
SUINV11JB2 | 6 | DC current input 5 | SU F3 INV11 | DcMs_Amp_05 | A | 30.5.3198
SUINV11JB2 | 7 | DC current input 6 | SU F3 INV11 | DcMs_Amp_06 | A | 30.5.3199
SUINV11JB2 | 8 | DC current input 7 | SU F3 INV11 | DcMs_Amp_07 | A | 30.5.3200
SUINV11JB2 | 9 | DC current input 8 | SU F3 INV11 | DcMs_Amp_08 | A | 30.5.3201
SUINV11JB2 | 10 | DC current input 9 | SU F3 INV11 | DcMs_Amp_09 | A | 30.5.3202
SUINV11JB2 | 11 | DC current input 10 | SU F3 INV11 | DcMs_Amp_10 | A | 30.5.3203
SUINV11JB2 | 12 | DC current input 11 | SU F3 INV11 | DcMs_Amp_11 | A | 30.5.3204
SUINV11JB2 | 13 | DC current input 12 | SU F3 INV11 | DcMs_Amp_12 | A | 30.5.3205
SUINV11JB2 | 14 | DC current input 13 | SU F3 INV11 | DcMs_Amp_13 | A | 30.5.3206
SUINV11JB2 | 15 | DC current input 14 | SU F3 INV11 | DcMs_Amp_14 | A | 30.5.3207
SUINV11JB2 | 16 | DC current input 15 | SU F3 INV11 | DcMs_Amp_15 | A | 30.5.3208
SUINV11JB2 | 17 | DC current input 16 | SU F3 INV11 | DcMs_Amp_16 | A | 30.5.3209
SUINV11JB2 | 18 | DC current input 1 | SU F3 INV11 | DcMs_Amp_01_F | A | 30.5.3210
SUINV11JB2 | 19 | DC current input 2 | SU F3 INV11 | DcMs_Amp_02_F | A | 30.5.3211
SUINV11JB2 | 20 | DC current input 3 | SU F3 INV11 | DcMs_Amp_03_F | A | 30.5.3212
SUINV11JB2 | 21 | DC current input 4 | SU F3 INV11 | DcMs_Amp_04_F | A | 30.5.3213
SUINV11JB2 | 22 | DC current input 5 | SU F3 INV11 | DcMs_Amp_05_F | A | 30.5.3214
SUINV11JB2 | 23 | DC current input 6 | SU F3 INV11 | DcMs_Amp_06_F | A | 30.5.3215
SUINV11JB2 | 24 | DC current input 7 | SU F3 INV11 | DcMs_Amp_07_F | A | 30.5.3216
SUINV11JB2 | 25 | DC current input 8 | SU F3 INV11 | DcMs_Amp_08_F | A | 30.5.3217
SUINV11JB2 | 26 | DC current input 9 | SU F3 INV11 | DcMs_Amp_09_F | A | 30.5.3218
SUINV11JB2 | 27 | DC current input 10 | SU F3 INV11 | DcMs_Amp_10_F | A | 30.5.3219
SUINV11JB2 | 28 | DC current input 11 | SU F3 INV11 | DcMs_Amp_11_F | A | 30.5.3220
SUINV11JB2 | 29 | DC current input 12 | SU F3 INV11 | DcMs_Amp_12_F | A | 30.5.3221
SUINV11JB2 | 30 | DC current input 13 | SU F3 INV11 | DcMs_Amp_13_F | A | 30.5.3222
SUINV11JB2 | 31 | DC current input 14 | SU F3 INV11 | DcMs_Amp_14_F | A | 30.5.3223
SUINV11JB2 | 32 | DC current input 15 | SU F3 INV11 | DcMs_Amp_15_F | A | 30.5.3224
SUINV11JB2 | 33 | DC current input 16 | SU F3 INV11 | DcMs_Amp_16_F | A | 30.5.3225
SUF3INV12 | 1 | DC voltage DC plus to DC minus | SU F3 INV12 | DcMs_Vol | V | 30.5.3226
SUF3INV12 | 2 | DC current inverter bridge 1 | SU F3 INV12 | DcMs_Amp_Stk1 | A | 30.5.3227
SUF3INV12 | 3 | DC current inverter bridge 2 | SU F3 INV12 | DcMs_Amp_Stk2 | A | 30.5.3228
SUF3INV12 | 4 | DC current inverter bridge 3 | SU F3 INV12 | DcMs_Amp_Stk3 | A | 30.5.3229
SUF3INV12 | 5 | DC current, total | SU F3 INV12 | DcMs_TotAmp | A | 30.5.3230
SUF3INV12 | 6 | DC power, total | SU F3 INV12 | DcMs_TotWatt | kW | 30.5.3231
SUF3INV12 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV12 | InvMs_DclVol_Stk1 | V | 30.5.3232
SUF3INV12 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV12 | InvMs_DclVol_Stk2 | V | 30.5.3233
SUF3INV12 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV12 | InvMs_DclVol_Stk3 | V | 30.5.3234
SUF3INV12 | 10 | AC current L1, total | SU F3 INV12 | InvMs_TotA_PhsA | A | 30.5.3235
SUF3INV12 | 11 | AC current L2, total | SU F3 INV12 | InvMs_TotA_PhsB | A | 30.5.3236
SUF3INV12 | 12 | AC current L3, total | SU F3 INV12 | InvMs_TotA_PhsC | A | 30.5.3237
SUF3INV12 | 13 | Power factor (cos phi) | SU F3 INV12 | InvMs_PF | "-" | 30.5.3238
SUF3INV12 | 14 | Apparent power, total | SU F3 INV12 | InvMs_TotVA | kVA | 30.5.3239
SUF3INV12 | 15 | Active power, total | SU F3 INV12 | InvMs_TotW | kW | 30.5.3240
SUF3INV12 | 16 | Reactive power, total | SU F3 INV12 | InvMs_TotVAr | kVAr | 30.5.3241
SUF3INV12 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV12 | GriMs_V_PhsAB | V | 30.5.3242
SUF3INV12 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV12 | GriMs_V_PhsBC | V | 30.5.3243
SUF3INV12 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV12 | GriMs_V_PhsCA | V | 30.5.3244
SUF3INV12 | 20 | Power frequency | SU F3 INV12 | GriMs_Hz | Hz | 30.5.3245
SUF3INV12 | 21 | Temperature in the AC range | SU F3 INV12 | TmpCab_Acc | °C | 30.5.3246
SUF3INV12 | 22 | Temperature in the DC range | SU F3 INV12 | TmpCab_Dcc | °C | 30.5.3247
SUF3INV12 | 23 | Temperature in the electronics area | SU F3 INV12 | TmpCab_Rio | °C | 30.5.3248
SUF3INV12 | 24 | Temperature in interior, maximum value | SU F3 INV12 | TmpCab_Max | °C | 30.5.3249
SUF3INV12 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV12 | TmpStk_IgbtMax | °C | 30.5.3250
SUF3INV12 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV12 | TmpStk_PcbMax | °C | 30.5.3251
SUF3INV12 | 27 | Outside temperature | SU F3 INV12 | TmpExl | ?C | 30.5.3252
SUF3INV12 | 28 | Temperature of the MV transformer | SU F3 INV12 | TmpTrf | °C | 30.5.3253
SUF3INV12 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV12 | DcSw1Stt | "-" | 30.5.3254
SUF3INV12 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV12 | DcSw2Stt | "-" | 30.5.3255
SUF3INV12 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV12 | DcSw3Stt | "-" | 30.5.3256
SUF3INV12 | 32 | Switching status of the AC circuit breaker | SU F3 INV12 | AcSwStt | "-" | 30.5.3257
SUF3INV12 | 33 | Switching state of the capacitor contactor | SU F3 INV12 | CapacSwStt | "-" | 30.5.3258
SUF3INV12 | 34 | Switching status of the pre-charging contactor | SU F3 INV12 | PrchrgSwStt | "-" | 30.5.3259
SUF3INV12 | 35 | Feed-in hours | SU F3 INV12 | Cnt_TotFeedTm | "-" | 30.5.3260
SUF3INV12 | 36 | Operating hours | SU F3 INV12 | Cnt_TotOpTm | "-" | 30.5.3261
SUF3INV12 | 37 | DC energy drawn, total | SU F3 INV12 | Cnt_TotWatthIn | MWh | 30.5.3262
SUF3INV12 | 38 | AC energy fed in, total | SU F3 INV12 | Cnt_TotWhOut | MWh | 30.5.3263
SUF3INV12 | 39 | DC energy drawn that day | SU F3 INV12 | Cnt_WatthIn | MWh | 30.5.3264
SUF3INV12 | 40 | AC energy fed in that day | SU F3 INV12 | Cnt_WhOut | MWh | 30.5.3265
SUF3INV12 | 41 | Operating hours of the interior fan 1 | SU F3 INV12 | Cnt_FanCab1Tm | "-" | 30.5.3266
SUF3INV12 | 42 | Operating hours of the interior fan 2 | SU F3 INV12 | Cnt_FanCab2Tm | "-" | 30.5.3267
SUF3INV12 | 43 | Operating hours of the inverter bridge fan | SU F3 INV12 | Cnt_FanStkTm | "-" | 30.5.3268
SUF3INV12 | 44 | Operating hours of the internal heating element | SU F3 INV12 | Cnt_HtCabTm | "-" | 30.5.3269
SUF3INV12 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV12 | Cnt_HtLoExlTmpTm | "-" | 30.5.3270
SUF3INV12 | 46 | Error location of the present error | SU F3 INV12 | ErrLcn | "-" | 30.5.3271
SUF3INV12 | 47 | Error status of the inverter | SU F3 INV12 | ErrStt | "-" | 30.5.3272
SUF3INV12 | 48 | Error number of the present error | SU F3 INV12 | ErrNo | "-" | 30.5.3273
SUF3INV12 | 49 | Operating state of the inverter | SU F3 INV12 | OpStt | "-" | 30.5.3274
SUF3INV12 | 50 | Switch status of the start-stop key switch | SU F3 INV12 | Rio_KeySw | "-" | 30.5.3275
SUF3INV12 | 51 | Waiting time for grid connection | SU F3 INV12 | WaitGriTm | s | 30.5.3276
SUF3INV12 | 52 | Inverter serial number | SU F3 INV12 | DevInf_SerNo | "-" | 30.5.3277
SUF3INV12 | 53 | Switching status of the GFDI | SU F3 INV12 | GfdiSwStt | "-" | 30.5.3278
SUF3INV12 | 54 | Active power, setpoint | SU F3 INV12 | WSpt | kW | 30.5.3279
SUF3INV12 | 55 | Maximum apparent power, setpoint | SU F3 INV12 | VAMaxSpt | kVA | 30.5.3280
SUF3INV12 | 56 | Reactive power, setpoint | SU F3 INV12 | VArSpt | kVAr | 30.5.3281
SUF3INV12 | 57 | Power factor cos (phi), setpoint | SU F3 INV12 | PFSpt | "-" | 30.5.3282
SUF3INV12 | 58 | Fast stop hermetic protection, pressure | SU F3 INV12 | TrfPro_Pres | "-" | 30.5.3283
SUF3INV12 | 59 | Fast stop hermetic protection, temperature | SU F3 INV12 | TrfPro_TmpTrp | "-" | 30.5.3284
SUF3INV12 | 60 | Hermetic protection, gas fill level | SU F3 INV12 | TrfPro_GasOilLev | "-" | 30.5.3285
SUF3INV12 | 61 | Hermetic pressure, temperature warning | SU F3 INV12 | TrfPro_TmpWrn | "-" | 30.5.3286
SUF3INV12 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV12 | TmpStk1_Igbt | °C | 30.5.3287
SUF3INV12 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV12 | TmpStk2_Igbt | °C | 30.5.3288
SUF3INV12 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV12 | TmpStk3_Igbt | °C | 30.5.3289
SUF3INV12 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV12 | TmpStk1_Pcb | ?C | 30.5.3290
SUF3INV12 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV12 | TmpStk2_Pcb | ?C | 30.5.3291
SUF3INV12 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV12 | TmpStk3_Pcb | ?C | 30.5.3292
SUF3INV12 | 68 | AC Energy Fed in the previous Day | SU F3 INV12 | Cnt_YstdWhOut | MWh | 30.5.3293
SUF3INV12 | 69 | CPU running time since system start | SU F3 INV12 | Cpu1UpTime | s | 30.5.3294
SUF3INV12 | 70 | Insulation resistance | SU F3 INV12 | PvGnd_RisIso | kOhm | 30.5.3295
SUF3INV12 | 71 | MV transformer pressure | SU F3 INV12 | PresTrf | "-" | 30.5.3296
SUF3INV12 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV12 | PresTrf_ErrStt | "-" | 30.5.3297
SUF3INV12 | 73 | DC voltage DC plus to DC minus | SU F3 INV12 | DcMs_Vol_F | V | 30.5.3298
SUF3INV12 | 74 | DC current inverter bridge 1 | SU F3 INV12 | DcMs_Amp_Stk1_F | A | 30.5.3299
SUF3INV12 | 75 | DC current inverter bridge 2 | SU F3 INV12 | DcMs_Amp_Stk2_F | A | 30.5.3300
SUF3INV12 | 76 | DC current inverter bridge 3 | SU F3 INV12 | DcMs_Amp_Stk3_F | A | 30.5.3301
SUF3INV12 | 77 | DC current, total | SU F3 INV12 | DcMs_TotAmp_F | A | 30.5.3302
SUF3INV12 | 78 | DC power, total | SU F3 INV12 | DcMs_TotWatt_F | kW | 30.5.3303
SUF3INV12 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV12 | InvMs_DclVol_Stk1_F | V | 30.5.3304
SUF3INV12 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV12 | InvMs_DclVol_Stk2_F | V | 30.5.3305
SUF3INV12 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV12 | InvMs_DclVol_Stk3_F | V | 30.5.3306
SUF3INV12 | 82 | AC current L1, total | SU F3 INV12 | InvMs_TotA_PhsA_F | A | 30.5.3307
SUF3INV12 | 83 | AC current L2, total | SU F3 INV12 | InvMs_TotA_PhsB_F | A | 30.5.3308
SUF3INV12 | 84 | AC current L3, total | SU F3 INV12 | InvMs_TotA_PhsC_F | A | 30.5.3309
SUF3INV12 | 85 | Power factor (cos phi) | SU F3 INV12 | InvMs_PF_F | "-" | 30.5.3310
SUF3INV12 | 86 | Active power, total | SU F3 INV12 | InvMs_TotW_F | kW | 30.5.3311
SUF3INV12 | 87 | Reactive power, total | SU F3 INV12 | InvMs_TotVAr_F | kVAr | 30.5.3312
SUF3INV12 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV12 | GriMs_V_PhsAB_F | V | 30.5.3313
SUF3INV12 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV12 | GriMs_V_PhsBC_F | V | 30.5.3314
SUF3INV12 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV12 | GriMs_V_PhsCA_F | V | 30.5.3315
SUF3INV12 | 91 | Power frequency | SU F3 INV12 | GriMs_Hz_F | Hz | 30.5.3316
SUF3INV12 | 92 | Temperature in the AC range | SU F3 INV12 | TmpCab_Acc_F | °C | 30.5.3317
SUF3INV12 | 93 | Temperature in the DC range | SU F3 INV12 | TmpCab_Dcc_F | °C | 30.5.3318
SUF3INV12 | 94 | Temperature in the electronics area | SU F3 INV12 | TmpCab_Rio_F | °C | 30.5.3319
SUF3INV12 | 95 | Temperature in interior, maximum value | SU F3 INV12 | TmpCab_Max_F | °C | 30.5.3320
SUF3INV12 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV12 | TmpStk_IgbtMax_F | °C | 30.5.3321
SUF3INV12 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV12 | TmpStk_PcbMax_F | °C | 30.5.3322
SUF3INV12 | 98 | Outside temperature | SU F3 INV12 | TmpExl_F | ?C | 30.5.3323
SUF3INV12 | 99 | Temperature of the MV transformer | SU F3 INV12 | TmpTrf_F | °C | 30.5.3324
SUF3INV12 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV12 | TmpStk1_Igbt_F | °C | 30.5.3325
SUF3INV12 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV12 | TmpStk2_Igbt_F | °C | 30.5.3326
SUF3INV12 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV12 | TmpStk3_Igbt_F | °C | 30.5.3327
SUF3INV12 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV12 | TmpStk1_Pcb_F | ?C | 30.5.3328
SUF3INV12 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV12 | TmpStk2_Pcb_F | ?C | 30.5.3329
SUF3INV12 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV12 | TmpStk3_Pcb_F | ?C | 30.5.3330
SUF3INV12 | 106 | MV transformer pressure | SU F3 INV12 | PresTrf_F | "-" | 30.5.3331
SUF3INV12 | 110 | Switching status of the DC load-break switch | SU F3 INV12 | DcSwStt | "-" | 30.5.3332
SUINV12JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV12 | Dat_UpdCnt_1 | "-" | 30.5.3333
SUINV12JB1 | 2 | DC current input 1 | SU F3 INV12 | DcMs_Amp_01 | A | 30.5.3334
SUINV12JB1 | 3 | DC current input 2 | SU F3 INV12 | DcMs_Amp_02 | A | 30.5.3335
SUINV12JB1 | 4 | DC current input 3 | SU F3 INV12 | DcMs_Amp_03 | A | 30.5.3336
SUINV12JB1 | 5 | DC current input 4 | SU F3 INV12 | DcMs_Amp_04 | A | 30.5.3337
SUINV12JB1 | 6 | DC current input 5 | SU F3 INV12 | DcMs_Amp_05 | A | 30.5.3338
SUINV12JB1 | 7 | DC current input 6 | SU F3 INV12 | DcMs_Amp_06 | A | 30.5.3339
SUINV12JB1 | 8 | DC current input 7 | SU F3 INV12 | DcMs_Amp_07 | A | 30.5.3340
SUINV12JB1 | 9 | DC current input 8 | SU F3 INV12 | DcMs_Amp_08 | A | 30.5.3341
SUINV12JB1 | 10 | DC current input 9 | SU F3 INV12 | DcMs_Amp_09 | A | 30.5.3342
SUINV12JB1 | 11 | DC current input 10 | SU F3 INV12 | DcMs_Amp_10 | A | 30.5.3343
SUINV12JB1 | 12 | DC current input 11 | SU F3 INV12 | DcMs_Amp_11 | A | 30.5.3344
SUINV12JB1 | 13 | DC current input 12 | SU F3 INV12 | DcMs_Amp_12 | A | 30.5.3345
SUINV12JB1 | 14 | DC current input 13 | SU F3 INV12 | DcMs_Amp_13 | A | 30.5.3346
SUINV12JB1 | 15 | DC current input 14 | SU F3 INV12 | DcMs_Amp_14 | A | 30.5.3347
SUINV12JB1 | 16 | DC current input 15 | SU F3 INV12 | DcMs_Amp_15 | A | 30.5.3348
SUINV12JB1 | 17 | DC current input 16 | SU F3 INV12 | DcMs_Amp_16 | A | 30.5.3349
SUINV12JB1 | 18 | DC current input 1 | SU F3 INV12 | DcMs_Amp_01_F | A | 30.5.3350
SUINV12JB1 | 19 | DC current input 2 | SU F3 INV12 | DcMs_Amp_02_F | A | 30.5.3351
SUINV12JB1 | 20 | DC current input 3 | SU F3 INV12 | DcMs_Amp_03_F | A | 30.5.3352
SUINV12JB1 | 21 | DC current input 4 | SU F3 INV12 | DcMs_Amp_04_F | A | 30.5.3353
SUINV12JB1 | 22 | DC current input 5 | SU F3 INV12 | DcMs_Amp_05_F | A | 30.5.3354
SUINV12JB1 | 23 | DC current input 6 | SU F3 INV12 | DcMs_Amp_06_F | A | 30.5.3355
SUINV12JB1 | 24 | DC current input 7 | SU F3 INV12 | DcMs_Amp_07_F | A | 30.5.3356
SUINV12JB1 | 25 | DC current input 8 | SU F3 INV12 | DcMs_Amp_08_F | A | 30.5.3357
SUINV12JB1 | 26 | DC current input 9 | SU F3 INV12 | DcMs_Amp_09_F | A | 30.5.3358
SUINV12JB1 | 27 | DC current input 10 | SU F3 INV12 | DcMs_Amp_10_F | A | 30.5.3359
SUINV12JB1 | 28 | DC current input 11 | SU F3 INV12 | DcMs_Amp_11_F | A | 30.5.3360
SUINV12JB1 | 29 | DC current input 12 | SU F3 INV12 | DcMs_Amp_12_F | A | 30.5.3361
SUINV12JB1 | 30 | DC current input 13 | SU F3 INV12 | DcMs_Amp_13_F | A | 30.5.3362
SUINV12JB1 | 31 | DC current input 14 | SU F3 INV12 | DcMs_Amp_14_F | A | 30.5.3363
SUINV12JB1 | 32 | DC current input 15 | SU F3 INV12 | DcMs_Amp_15_F | A | 30.5.3364
SUINV12JB1 | 33 | DC current input 16 | SU F3 INV12 | DcMs_Amp_16_F | A | 30.5.3365
SUINV12JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV12 | Dat_UpdCnt_1 | "-" | 30.5.3366
SUINV12JB2 | 2 | DC current input 1 | SU F3 INV12 | DcMs_Amp_01 | A | 30.5.3367
SUINV12JB2 | 3 | DC current input 2 | SU F3 INV12 | DcMs_Amp_02 | A | 30.5.3368
SUINV12JB2 | 4 | DC current input 3 | SU F3 INV12 | DcMs_Amp_03 | A | 30.5.3369
SUINV12JB2 | 5 | DC current input 4 | SU F3 INV12 | DcMs_Amp_04 | A | 30.5.3370
SUINV12JB2 | 6 | DC current input 5 | SU F3 INV12 | DcMs_Amp_05 | A | 30.5.3371
SUINV12JB2 | 7 | DC current input 6 | SU F3 INV12 | DcMs_Amp_06 | A | 30.5.3372
SUINV12JB2 | 8 | DC current input 7 | SU F3 INV12 | DcMs_Amp_07 | A | 30.5.3373
SUINV12JB2 | 9 | DC current input 8 | SU F3 INV12 | DcMs_Amp_08 | A | 30.5.3374
SUINV12JB2 | 10 | DC current input 9 | SU F3 INV12 | DcMs_Amp_09 | A | 30.5.3375
SUINV12JB2 | 11 | DC current input 10 | SU F3 INV12 | DcMs_Amp_10 | A | 30.5.3376
SUINV12JB2 | 12 | DC current input 11 | SU F3 INV12 | DcMs_Amp_11 | A | 30.5.3377
SUINV12JB2 | 13 | DC current input 12 | SU F3 INV12 | DcMs_Amp_12 | A | 30.5.3378
SUINV12JB2 | 14 | DC current input 13 | SU F3 INV12 | DcMs_Amp_13 | A | 30.5.3379
SUINV12JB2 | 15 | DC current input 14 | SU F3 INV12 | DcMs_Amp_14 | A | 30.5.3380
SUINV12JB2 | 16 | DC current input 15 | SU F3 INV12 | DcMs_Amp_15 | A | 30.5.3381
SUINV12JB2 | 17 | DC current input 16 | SU F3 INV12 | DcMs_Amp_16 | A | 30.5.3382
SUINV12JB2 | 18 | DC current input 1 | SU F3 INV12 | DcMs_Amp_01_F | A | 30.5.3383
SUINV12JB2 | 19 | DC current input 2 | SU F3 INV12 | DcMs_Amp_02_F | A | 30.5.3384
SUINV12JB2 | 20 | DC current input 3 | SU F3 INV12 | DcMs_Amp_03_F | A | 30.5.3385
SUINV12JB2 | 21 | DC current input 4 | SU F3 INV12 | DcMs_Amp_04_F | A | 30.5.3386
SUINV12JB2 | 22 | DC current input 5 | SU F3 INV12 | DcMs_Amp_05_F | A | 30.5.3387
SUINV12JB2 | 23 | DC current input 6 | SU F3 INV12 | DcMs_Amp_06_F | A | 30.5.3388
SUINV12JB2 | 24 | DC current input 7 | SU F3 INV12 | DcMs_Amp_07_F | A | 30.5.3389
SUINV12JB2 | 25 | DC current input 8 | SU F3 INV12 | DcMs_Amp_08_F | A | 30.5.3390
SUINV12JB2 | 26 | DC current input 9 | SU F3 INV12 | DcMs_Amp_09_F | A | 30.5.3391
SUINV12JB2 | 27 | DC current input 10 | SU F3 INV12 | DcMs_Amp_10_F | A | 30.5.3392
SUINV12JB2 | 28 | DC current input 11 | SU F3 INV12 | DcMs_Amp_11_F | A | 30.5.3393
SUINV12JB2 | 29 | DC current input 12 | SU F3 INV12 | DcMs_Amp_12_F | A | 30.5.3394
SUINV12JB2 | 30 | DC current input 13 | SU F3 INV12 | DcMs_Amp_13_F | A | 30.5.3395
SUINV12JB2 | 31 | DC current input 14 | SU F3 INV12 | DcMs_Amp_14_F | A | 30.5.3396
SUINV12JB2 | 32 | DC current input 15 | SU F3 INV12 | DcMs_Amp_15_F | A | 30.5.3397
SUINV12JB2 | 33 | DC current input 16 | SU F3 INV12 | DcMs_Amp_16_F | A | 30.5.3398
SUF3INV14 | 1 | DC voltage DC plus to DC minus | SU F3 INV14 | DcMs_Vol | V | 30.5.3399
SUF3INV14 | 2 | DC current inverter bridge 1 | SU F3 INV14 | DcMs_Amp_Stk1 | A | 30.5.3400
SUF3INV14 | 3 | DC current inverter bridge 2 | SU F3 INV14 | DcMs_Amp_Stk2 | A | 30.5.3401
SUF3INV14 | 4 | DC current inverter bridge 3 | SU F3 INV14 | DcMs_Amp_Stk3 | A | 30.5.3402
SUF3INV14 | 5 | DC current, total | SU F3 INV14 | DcMs_TotAmp | A | 30.5.3403
SUF3INV14 | 6 | DC power, total | SU F3 INV14 | DcMs_TotWatt | kW | 30.5.3404
SUF3INV14 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV14 | InvMs_DclVol_Stk1 | V | 30.5.3405
SUF3INV14 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV14 | InvMs_DclVol_Stk2 | V | 30.5.3406
SUF3INV14 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV14 | InvMs_DclVol_Stk3 | V | 30.5.3407
SUF3INV14 | 10 | AC current L1, total | SU F3 INV14 | InvMs_TotA_PhsA | A | 30.5.3408
SUF3INV14 | 11 | AC current L2, total | SU F3 INV14 | InvMs_TotA_PhsB | A | 30.5.3409
SUF3INV14 | 12 | AC current L3, total | SU F3 INV14 | InvMs_TotA_PhsC | A | 30.5.3410
SUF3INV14 | 13 | Power factor (cos phi) | SU F3 INV14 | InvMs_PF | "-" | 30.5.3411
SUF3INV14 | 14 | Apparent power, total | SU F3 INV14 | InvMs_TotVA | kVA | 30.5.3412
SUF3INV14 | 15 | Active power, total | SU F3 INV14 | InvMs_TotW | kW | 30.5.3413
SUF3INV14 | 16 | Reactive power, total | SU F3 INV14 | InvMs_TotVAr | kVAr | 30.5.3414
SUF3INV14 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV14 | GriMs_V_PhsAB | V | 30.5.3415
SUF3INV14 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV14 | GriMs_V_PhsBC | V | 30.5.3416
SUF3INV14 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV14 | GriMs_V_PhsCA | V | 30.5.3417
SUF3INV14 | 20 | Power frequency | SU F3 INV14 | GriMs_Hz | Hz | 30.5.3418
SUF3INV14 | 21 | Temperature in the AC range | SU F3 INV14 | TmpCab_Acc | °C | 30.5.3419
SUF3INV14 | 22 | Temperature in the DC range | SU F3 INV14 | TmpCab_Dcc | °C | 30.5.3420
SUF3INV14 | 23 | Temperature in the electronics area | SU F3 INV14 | TmpCab_Rio | °C | 30.5.3421
SUF3INV14 | 24 | Temperature in interior, maximum value | SU F3 INV14 | TmpCab_Max | °C | 30.5.3422
SUF3INV14 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV14 | TmpStk_IgbtMax | °C | 30.5.3423
SUF3INV14 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV14 | TmpStk_PcbMax | °C | 30.5.3424
SUF3INV14 | 27 | Outside temperature | SU F3 INV14 | TmpExl | ?C | 30.5.3425
SUF3INV14 | 28 | Temperature of the MV transformer | SU F3 INV14 | TmpTrf | °C | 30.5.3426
SUF3INV14 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV14 | DcSw1Stt | "-" | 30.5.3427
SUF3INV14 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV14 | DcSw2Stt | "-" | 30.5.3428
SUF3INV14 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV14 | DcSw3Stt | "-" | 30.5.3429
SUF3INV14 | 32 | Switching status of the AC circuit breaker | SU F3 INV14 | AcSwStt | "-" | 30.5.3430
SUF3INV14 | 33 | Switching state of the capacitor contactor | SU F3 INV14 | CapacSwStt | "-" | 30.5.3431
SUF3INV14 | 34 | Switching status of the pre-charging contactor | SU F3 INV14 | PrchrgSwStt | "-" | 30.5.3432
SUF3INV14 | 35 | Feed-in hours | SU F3 INV14 | Cnt_TotFeedTm | "-" | 30.5.3433
SUF3INV14 | 36 | Operating hours | SU F3 INV14 | Cnt_TotOpTm | "-" | 30.5.3434
SUF3INV14 | 37 | DC energy drawn, total | SU F3 INV14 | Cnt_TotWatthIn | MWh | 30.5.3435
SUF3INV14 | 38 | AC energy fed in, total | SU F3 INV14 | Cnt_TotWhOut | MWh | 30.5.3436
SUF3INV14 | 39 | DC energy drawn that day | SU F3 INV14 | Cnt_WatthIn | MWh | 30.5.3437
SUF3INV14 | 40 | AC energy fed in that day | SU F3 INV14 | Cnt_WhOut | MWh | 30.5.3438
SUF3INV14 | 41 | Operating hours of the interior fan 1 | SU F3 INV14 | Cnt_FanCab1Tm | "-" | 30.5.3439
SUF3INV14 | 42 | Operating hours of the interior fan 2 | SU F3 INV14 | Cnt_FanCab2Tm | "-" | 30.5.3440
SUF3INV14 | 43 | Operating hours of the inverter bridge fan | SU F3 INV14 | Cnt_FanStkTm | "-" | 30.5.3441
SUF3INV14 | 44 | Operating hours of the internal heating element | SU F3 INV14 | Cnt_HtCabTm | "-" | 30.5.3442
SUF3INV14 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV14 | Cnt_HtLoExlTmpTm | "-" | 30.5.3443
SUF3INV14 | 46 | Error location of the present error | SU F3 INV14 | ErrLcn | "-" | 30.5.3444
SUF3INV14 | 47 | Error status of the inverter | SU F3 INV14 | ErrStt | "-" | 30.5.3445
SUF3INV14 | 48 | Error number of the present error | SU F3 INV14 | ErrNo | "-" | 30.5.3446
SUF3INV14 | 49 | Operating state of the inverter | SU F3 INV14 | OpStt | "-" | 30.5.3447
SUF3INV14 | 50 | Switch status of the start-stop key switch | SU F3 INV14 | Rio_KeySw | "-" | 30.5.3448
SUF3INV14 | 51 | Waiting time for grid connection | SU F3 INV14 | WaitGriTm | s | 30.5.3449
SUF3INV14 | 52 | Inverter serial number | SU F3 INV14 | DevInf_SerNo | "-" | 30.5.3450
SUF3INV14 | 53 | Switching status of the GFDI | SU F3 INV14 | GfdiSwStt | "-" | 30.5.3451
SUF3INV14 | 54 | Active power, setpoint | SU F3 INV14 | WSpt | kW | 30.5.3452
SUF3INV14 | 55 | Maximum apparent power, setpoint | SU F3 INV14 | VAMaxSpt | kVA | 30.5.3453
SUF3INV14 | 56 | Reactive power, setpoint | SU F3 INV14 | VArSpt | kVAr | 30.5.3454
SUF3INV14 | 57 | Power factor cos (phi), setpoint | SU F3 INV14 | PFSpt | "-" | 30.5.3455
SUF3INV14 | 58 | Fast stop hermetic protection, pressure | SU F3 INV14 | TrfPro_Pres | "-" | 30.5.3456
SUF3INV14 | 59 | Fast stop hermetic protection, temperature | SU F3 INV14 | TrfPro_TmpTrp | "-" | 30.5.3457
SUF3INV14 | 60 | Hermetic protection, gas fill level | SU F3 INV14 | TrfPro_GasOilLev | "-" | 30.5.3458
SUF3INV14 | 61 | Hermetic pressure, temperature warning | SU F3 INV14 | TrfPro_TmpWrn | "-" | 30.5.3459
SUF3INV14 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV14 | TmpStk1_Igbt | °C | 30.5.3460
SUF3INV14 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV14 | TmpStk2_Igbt | °C | 30.5.3461
SUF3INV14 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV14 | TmpStk3_Igbt | °C | 30.5.3462
SUF3INV14 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV14 | TmpStk1_Pcb | ?C | 30.5.3463
SUF3INV14 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV14 | TmpStk2_Pcb | ?C | 30.5.3464
SUF3INV14 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV14 | TmpStk3_Pcb | ?C | 30.5.3465
SUF3INV14 | 68 | AC Energy Fed in the previous Day | SU F3 INV14 | Cnt_YstdWhOut | MWh | 30.5.3466
SUF3INV14 | 69 | CPU running time since system start | SU F3 INV14 | Cpu1UpTime | s | 30.5.3467
SUF3INV14 | 70 | Insulation resistance | SU F3 INV14 | PvGnd_RisIso | kOhm | 30.5.3468
SUF3INV14 | 71 | MV transformer pressure | SU F3 INV14 | PresTrf | "-" | 30.5.3469
SUF3INV14 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV14 | PresTrf_ErrStt | "-" | 30.5.3470
SUF3INV14 | 73 | DC voltage DC plus to DC minus | SU F3 INV14 | DcMs_Vol_F | V | 30.5.3471
SUF3INV14 | 74 | DC current inverter bridge 1 | SU F3 INV14 | DcMs_Amp_Stk1_F | A | 30.5.3472
SUF3INV14 | 75 | DC current inverter bridge 2 | SU F3 INV14 | DcMs_Amp_Stk2_F | A | 30.5.3473
SUF3INV14 | 76 | DC current inverter bridge 3 | SU F3 INV14 | DcMs_Amp_Stk3_F | A | 30.5.3474
SUF3INV14 | 77 | DC current, total | SU F3 INV14 | DcMs_TotAmp_F | A | 30.5.3475
SUF3INV14 | 78 | DC power, total | SU F3 INV14 | DcMs_TotWatt_F | kW | 30.5.3476
SUF3INV14 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV14 | InvMs_DclVol_Stk1_F | V | 30.5.3477
SUF3INV14 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV14 | InvMs_DclVol_Stk2_F | V | 30.5.3478
SUF3INV14 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV14 | InvMs_DclVol_Stk3_F | V | 30.5.3479
SUF3INV14 | 82 | AC current L1, total | SU F3 INV14 | InvMs_TotA_PhsA_F | A | 30.5.3480
SUF3INV14 | 83 | AC current L2, total | SU F3 INV14 | InvMs_TotA_PhsB_F | A | 30.5.3481
SUF3INV14 | 84 | AC current L3, total | SU F3 INV14 | InvMs_TotA_PhsC_F | A | 30.5.3482
SUF3INV14 | 85 | Power factor (cos phi) | SU F3 INV14 | InvMs_PF_F | "-" | 30.5.3483
SUF3INV14 | 86 | Active power, total | SU F3 INV14 | InvMs_TotW_F | kW | 30.5.3484
SUF3INV14 | 87 | Reactive power, total | SU F3 INV14 | InvMs_TotVAr_F | kVAr | 30.5.3485
SUF3INV14 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV14 | GriMs_V_PhsAB_F | V | 30.5.3486
SUF3INV14 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV14 | GriMs_V_PhsBC_F | V | 30.5.3487
SUF3INV14 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV14 | GriMs_V_PhsCA_F | V | 30.5.3488
SUF3INV14 | 91 | Power frequency | SU F3 INV14 | GriMs_Hz_F | Hz | 30.5.3489
SUF3INV14 | 92 | Temperature in the AC range | SU F3 INV14 | TmpCab_Acc_F | °C | 30.5.3490
SUF3INV14 | 93 | Temperature in the DC range | SU F3 INV14 | TmpCab_Dcc_F | °C | 30.5.3491
SUF3INV14 | 94 | Temperature in the electronics area | SU F3 INV14 | TmpCab_Rio_F | °C | 30.5.3492
SUF3INV14 | 95 | Temperature in interior, maximum value | SU F3 INV14 | TmpCab_Max_F | °C | 30.5.3493
SUF3INV14 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV14 | TmpStk_IgbtMax_F | °C | 30.5.3494
SUF3INV14 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV14 | TmpStk_PcbMax_F | °C | 30.5.3495
SUF3INV14 | 98 | Outside temperature | SU F3 INV14 | TmpExl_F | ?C | 30.5.3496
SUF3INV14 | 99 | Temperature of the MV transformer | SU F3 INV14 | TmpTrf_F | °C | 30.5.3497
SUF3INV14 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV14 | TmpStk1_Igbt_F | °C | 30.5.3498
SUF3INV14 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV14 | TmpStk2_Igbt_F | °C | 30.5.3499
SUF3INV14 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV14 | TmpStk3_Igbt_F | °C | 30.5.3500
SUF3INV14 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV14 | TmpStk1_Pcb_F | ?C | 30.5.3501
SUF3INV14 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV14 | TmpStk2_Pcb_F | ?C | 30.5.3502
SUF3INV14 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV14 | TmpStk3_Pcb_F | ?C | 30.5.3503
SUF3INV14 | 106 | MV transformer pressure | SU F3 INV14 | PresTrf_F | "-" | 30.5.3504
SUF3INV14 | 110 | Switching status of the DC load-break switch | SU F3 INV14 | DcSwStt | "-" | 30.5.3505
SUINV14JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV14 | Dat_UpdCnt_1 | "-" | 30.5.3506
SUINV14JB1 | 2 | DC current input 1 | SU F3 INV14 | DcMs_Amp_01 | A | 30.5.3507
SUINV14JB1 | 3 | DC current input 2 | SU F3 INV14 | DcMs_Amp_02 | A | 30.5.3508
SUINV14JB1 | 4 | DC current input 3 | SU F3 INV14 | DcMs_Amp_03 | A | 30.5.3509
SUINV14JB1 | 5 | DC current input 4 | SU F3 INV14 | DcMs_Amp_04 | A | 30.5.3510
SUINV14JB1 | 6 | DC current input 5 | SU F3 INV14 | DcMs_Amp_05 | A | 30.5.3511
SUINV14JB1 | 7 | DC current input 6 | SU F3 INV14 | DcMs_Amp_06 | A | 30.5.3512
SUINV14JB1 | 8 | DC current input 7 | SU F3 INV14 | DcMs_Amp_07 | A | 30.5.3513
SUINV14JB1 | 9 | DC current input 8 | SU F3 INV14 | DcMs_Amp_08 | A | 30.5.3514
SUINV14JB1 | 10 | DC current input 9 | SU F3 INV14 | DcMs_Amp_09 | A | 30.5.3515
SUINV14JB1 | 11 | DC current input 10 | SU F3 INV14 | DcMs_Amp_10 | A | 30.5.3516
SUINV14JB1 | 12 | DC current input 11 | SU F3 INV14 | DcMs_Amp_11 | A | 30.5.3517
SUINV14JB1 | 13 | DC current input 12 | SU F3 INV14 | DcMs_Amp_12 | A | 30.5.3518
SUINV14JB1 | 14 | DC current input 13 | SU F3 INV14 | DcMs_Amp_13 | A | 30.5.3519
SUINV14JB1 | 15 | DC current input 14 | SU F3 INV14 | DcMs_Amp_14 | A | 30.5.3520
SUINV14JB1 | 16 | DC current input 15 | SU F3 INV14 | DcMs_Amp_15 | A | 30.5.3521
SUINV14JB1 | 17 | DC current input 16 | SU F3 INV14 | DcMs_Amp_16 | A | 30.5.3522
SUINV14JB1 | 18 | DC current input 1 | SU F3 INV14 | DcMs_Amp_01_F | A | 30.5.3523
SUINV14JB1 | 19 | DC current input 2 | SU F3 INV14 | DcMs_Amp_02_F | A | 30.5.3524
SUINV14JB1 | 20 | DC current input 3 | SU F3 INV14 | DcMs_Amp_03_F | A | 30.5.3525
SUINV14JB1 | 21 | DC current input 4 | SU F3 INV14 | DcMs_Amp_04_F | A | 30.5.3526
SUINV14JB1 | 22 | DC current input 5 | SU F3 INV14 | DcMs_Amp_05_F | A | 30.5.3527
SUINV14JB1 | 23 | DC current input 6 | SU F3 INV14 | DcMs_Amp_06_F | A | 30.5.3528
SUINV14JB1 | 24 | DC current input 7 | SU F3 INV14 | DcMs_Amp_07_F | A | 30.5.3529
SUINV14JB1 | 25 | DC current input 8 | SU F3 INV14 | DcMs_Amp_08_F | A | 30.5.3530
SUINV14JB1 | 26 | DC current input 9 | SU F3 INV14 | DcMs_Amp_09_F | A | 30.5.3531
SUINV14JB1 | 27 | DC current input 10 | SU F3 INV14 | DcMs_Amp_10_F | A | 30.5.3532
SUINV14JB1 | 28 | DC current input 11 | SU F3 INV14 | DcMs_Amp_11_F | A | 30.5.3533
SUINV14JB1 | 29 | DC current input 12 | SU F3 INV14 | DcMs_Amp_12_F | A | 30.5.3534
SUINV14JB1 | 30 | DC current input 13 | SU F3 INV14 | DcMs_Amp_13_F | A | 30.5.3535
SUINV14JB1 | 31 | DC current input 14 | SU F3 INV14 | DcMs_Amp_14_F | A | 30.5.3536
SUINV14JB1 | 32 | DC current input 15 | SU F3 INV14 | DcMs_Amp_15_F | A | 30.5.3537
SUINV14JB1 | 33 | DC current input 16 | SU F3 INV14 | DcMs_Amp_16_F | A | 30.5.3538
SUINV14JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV14 | Dat_UpdCnt_1 | "-" | 30.5.3539
SUINV14JB2 | 2 | DC current input 1 | SU F3 INV14 | DcMs_Amp_01 | A | 30.5.3540
SUINV14JB2 | 3 | DC current input 2 | SU F3 INV14 | DcMs_Amp_02 | A | 30.5.3541
SUINV14JB2 | 4 | DC current input 3 | SU F3 INV14 | DcMs_Amp_03 | A | 30.5.3542
SUINV14JB2 | 5 | DC current input 4 | SU F3 INV14 | DcMs_Amp_04 | A | 30.5.3543
SUINV14JB2 | 6 | DC current input 5 | SU F3 INV14 | DcMs_Amp_05 | A | 30.5.3544
SUINV14JB2 | 7 | DC current input 6 | SU F3 INV14 | DcMs_Amp_06 | A | 30.5.3545
SUINV14JB2 | 8 | DC current input 7 | SU F3 INV14 | DcMs_Amp_07 | A | 30.5.3546
SUINV14JB2 | 9 | DC current input 8 | SU F3 INV14 | DcMs_Amp_08 | A | 30.5.3547
SUINV14JB2 | 10 | DC current input 9 | SU F3 INV14 | DcMs_Amp_09 | A | 30.5.3548
SUINV14JB2 | 11 | DC current input 10 | SU F3 INV14 | DcMs_Amp_10 | A | 30.5.3549
SUINV14JB2 | 12 | DC current input 11 | SU F3 INV14 | DcMs_Amp_11 | A | 30.5.3550
SUINV14JB2 | 13 | DC current input 12 | SU F3 INV14 | DcMs_Amp_12 | A | 30.5.3551
SUINV14JB2 | 14 | DC current input 13 | SU F3 INV14 | DcMs_Amp_13 | A | 30.5.3552
SUINV14JB2 | 15 | DC current input 14 | SU F3 INV14 | DcMs_Amp_14 | A | 30.5.3553
SUINV14JB2 | 16 | DC current input 15 | SU F3 INV14 | DcMs_Amp_15 | A | 30.5.3554
SUINV14JB2 | 17 | DC current input 16 | SU F3 INV14 | DcMs_Amp_16 | A | 30.5.3555
SUINV14JB2 | 18 | DC current input 1 | SU F3 INV14 | DcMs_Amp_01_F | A | 30.5.3556
SUINV14JB2 | 19 | DC current input 2 | SU F3 INV14 | DcMs_Amp_02_F | A | 30.5.3557
SUINV14JB2 | 20 | DC current input 3 | SU F3 INV14 | DcMs_Amp_03_F | A | 30.5.3558
SUINV14JB2 | 21 | DC current input 4 | SU F3 INV14 | DcMs_Amp_04_F | A | 30.5.3559
SUINV14JB2 | 22 | DC current input 5 | SU F3 INV14 | DcMs_Amp_05_F | A | 30.5.3560
SUINV14JB2 | 23 | DC current input 6 | SU F3 INV14 | DcMs_Amp_06_F | A | 30.5.3561
SUINV14JB2 | 24 | DC current input 7 | SU F3 INV14 | DcMs_Amp_07_F | A | 30.5.3562
SUINV14JB2 | 25 | DC current input 8 | SU F3 INV14 | DcMs_Amp_08_F | A | 30.5.3563
SUINV14JB2 | 26 | DC current input 9 | SU F3 INV14 | DcMs_Amp_09_F | A | 30.5.3564
SUINV14JB2 | 27 | DC current input 10 | SU F3 INV14 | DcMs_Amp_10_F | A | 30.5.3565
SUINV14JB2 | 28 | DC current input 11 | SU F3 INV14 | DcMs_Amp_11_F | A | 30.5.3566
SUINV14JB2 | 29 | DC current input 12 | SU F3 INV14 | DcMs_Amp_12_F | A | 30.5.3567
SUINV14JB2 | 30 | DC current input 13 | SU F3 INV14 | DcMs_Amp_13_F | A | 30.5.3568
SUINV14JB2 | 31 | DC current input 14 | SU F3 INV14 | DcMs_Amp_14_F | A | 30.5.3569
SUINV14JB2 | 32 | DC current input 15 | SU F3 INV14 | DcMs_Amp_15_F | A | 30.5.3570
SUINV14JB2 | 33 | DC current input 16 | SU F3 INV14 | DcMs_Amp_16_F | A | 30.5.3571
SUF3INV17 | 1 | DC voltage DC plus to DC minus | SU F3 INV17 | DcMs_Vol | V | 30.5.3572
SUF3INV17 | 2 | DC current inverter bridge 1 | SU F3 INV17 | DcMs_Amp_Stk1 | A | 30.5.3573
SUF3INV17 | 3 | DC current inverter bridge 2 | SU F3 INV17 | DcMs_Amp_Stk2 | A | 30.5.3574
SUF3INV17 | 4 | DC current inverter bridge 3 | SU F3 INV17 | DcMs_Amp_Stk3 | A | 30.5.3575
SUF3INV17 | 5 | DC current, total | SU F3 INV17 | DcMs_TotAmp | A | 30.5.3576
SUF3INV17 | 6 | DC power, total | SU F3 INV17 | DcMs_TotWatt | kW | 30.5.3577
SUF3INV17 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV17 | InvMs_DclVol_Stk1 | V | 30.5.3578
SUF3INV17 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV17 | InvMs_DclVol_Stk2 | V | 30.5.3579
SUF3INV17 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV17 | InvMs_DclVol_Stk3 | V | 30.5.3580
SUF3INV17 | 10 | AC current L1, total | SU F3 INV17 | InvMs_TotA_PhsA | A | 30.5.3581
SUF3INV17 | 11 | AC current L2, total | SU F3 INV17 | InvMs_TotA_PhsB | A | 30.5.3582
SUF3INV17 | 12 | AC current L3, total | SU F3 INV17 | InvMs_TotA_PhsC | A | 30.5.3583
SUF3INV17 | 13 | Power factor (cos phi) | SU F3 INV17 | InvMs_PF | "-" | 30.5.3584
SUF3INV17 | 14 | Apparent power, total | SU F3 INV17 | InvMs_TotVA | kVA | 30.5.3585
SUF3INV17 | 15 | Active power, total | SU F3 INV17 | InvMs_TotW | kW | 30.5.3586
SUF3INV17 | 16 | Reactive power, total | SU F3 INV17 | InvMs_TotVAr | kVAr | 30.5.3587
SUF3INV17 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV17 | GriMs_V_PhsAB | V | 30.5.3588
SUF3INV17 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV17 | GriMs_V_PhsBC | V | 30.5.3589
SUF3INV17 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV17 | GriMs_V_PhsCA | V | 30.5.3590
SUF3INV17 | 20 | Power frequency | SU F3 INV17 | GriMs_Hz | Hz | 30.5.3591
SUF3INV17 | 21 | Temperature in the AC range | SU F3 INV17 | TmpCab_Acc | °C | 30.5.3592
SUF3INV17 | 22 | Temperature in the DC range | SU F3 INV17 | TmpCab_Dcc | °C | 30.5.3593
SUF3INV17 | 23 | Temperature in the electronics area | SU F3 INV17 | TmpCab_Rio | °C | 30.5.3594
SUF3INV17 | 24 | Temperature in interior, maximum value | SU F3 INV17 | TmpCab_Max | °C | 30.5.3595
SUF3INV17 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV17 | TmpStk_IgbtMax | °C | 30.5.3596
SUF3INV17 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV17 | TmpStk_PcbMax | °C | 30.5.3597
SUF3INV17 | 27 | Outside temperature | SU F3 INV17 | TmpExl | ?C | 30.5.3598
SUF3INV17 | 28 | Temperature of the MV transformer | SU F3 INV17 | TmpTrf | °C | 30.5.3599
SUF3INV17 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV17 | DcSw1Stt | "-" | 30.5.3600
SUF3INV17 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV17 | DcSw2Stt | "-" | 30.5.3601
SUF3INV17 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV17 | DcSw3Stt | "-" | 30.5.3602
SUF3INV17 | 32 | Switching status of the AC circuit breaker | SU F3 INV17 | AcSwStt | "-" | 30.5.3603
SUF3INV17 | 33 | Switching state of the capacitor contactor | SU F3 INV17 | CapacSwStt | "-" | 30.5.3604
SUF3INV17 | 34 | Switching status of the pre-charging contactor | SU F3 INV17 | PrchrgSwStt | "-" | 30.5.3605
SUF3INV17 | 35 | Feed-in hours | SU F3 INV17 | Cnt_TotFeedTm | "-" | 30.5.3606
SUF3INV17 | 36 | Operating hours | SU F3 INV17 | Cnt_TotOpTm | "-" | 30.5.3607
SUF3INV17 | 37 | DC energy drawn, total | SU F3 INV17 | Cnt_TotWatthIn | MWh | 30.5.3608
SUF3INV17 | 38 | AC energy fed in, total | SU F3 INV17 | Cnt_TotWhOut | MWh | 30.5.3609
SUF3INV17 | 39 | DC energy drawn that day | SU F3 INV17 | Cnt_WatthIn | MWh | 30.5.3610
SUF3INV17 | 40 | AC energy fed in that day | SU F3 INV17 | Cnt_WhOut | MWh | 30.5.3611
SUF3INV17 | 41 | Operating hours of the interior fan 1 | SU F3 INV17 | Cnt_FanCab1Tm | "-" | 30.5.3612
SUF3INV17 | 42 | Operating hours of the interior fan 2 | SU F3 INV17 | Cnt_FanCab2Tm | "-" | 30.5.3613
SUF3INV17 | 43 | Operating hours of the inverter bridge fan | SU F3 INV17 | Cnt_FanStkTm | "-" | 30.5.3614
SUF3INV17 | 44 | Operating hours of the internal heating element | SU F3 INV17 | Cnt_HtCabTm | "-" | 30.5.3615
SUF3INV17 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV17 | Cnt_HtLoExlTmpTm | "-" | 30.5.3616
SUF3INV17 | 46 | Error location of the present error | SU F3 INV17 | ErrLcn | "-" | 30.5.3617
SUF3INV17 | 47 | Error status of the inverter | SU F3 INV17 | ErrStt | "-" | 30.5.3618
SUF3INV17 | 48 | Error number of the present error | SU F3 INV17 | ErrNo | "-" | 30.5.3619
SUF3INV17 | 49 | Operating state of the inverter | SU F3 INV17 | OpStt | "-" | 30.5.3620
SUF3INV17 | 50 | Switch status of the start-stop key switch | SU F3 INV17 | Rio_KeySw | "-" | 30.5.3621
SUF3INV17 | 51 | Waiting time for grid connection | SU F3 INV17 | WaitGriTm | s | 30.5.3622
SUF3INV17 | 52 | Inverter serial number | SU F3 INV17 | DevInf_SerNo | "-" | 30.5.3623
SUF3INV17 | 53 | Switching status of the GFDI | SU F3 INV17 | GfdiSwStt | "-" | 30.5.3624
SUF3INV17 | 54 | Active power, setpoint | SU F3 INV17 | WSpt | kW | 30.5.3625
SUF3INV17 | 55 | Maximum apparent power, setpoint | SU F3 INV17 | VAMaxSpt | kVA | 30.5.3626
SUF3INV17 | 56 | Reactive power, setpoint | SU F3 INV17 | VArSpt | kVAr | 30.5.3627
SUF3INV17 | 57 | Power factor cos (phi), setpoint | SU F3 INV17 | PFSpt | "-" | 30.5.3628
SUF3INV17 | 58 | Fast stop hermetic protection, pressure | SU F3 INV17 | TrfPro_Pres | "-" | 30.5.3629
SUF3INV17 | 59 | Fast stop hermetic protection, temperature | SU F3 INV17 | TrfPro_TmpTrp | "-" | 30.5.3630
SUF3INV17 | 60 | Hermetic protection, gas fill level | SU F3 INV17 | TrfPro_GasOilLev | "-" | 30.5.3631
SUF3INV17 | 61 | Hermetic pressure, temperature warning | SU F3 INV17 | TrfPro_TmpWrn | "-" | 30.5.3632
SUF3INV17 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV17 | TmpStk1_Igbt | °C | 30.5.3633
SUF3INV17 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV17 | TmpStk2_Igbt | °C | 30.5.3634
SUF3INV17 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV17 | TmpStk3_Igbt | °C | 30.5.3635
SUF3INV17 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV17 | TmpStk1_Pcb | ?C | 30.5.3636
SUF3INV17 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV17 | TmpStk2_Pcb | ?C | 30.5.3637
SUF3INV17 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV17 | TmpStk3_Pcb | ?C | 30.5.3638
SUF3INV17 | 68 | AC Energy Fed in the previous Day | SU F3 INV17 | Cnt_YstdWhOut | MWh | 30.5.3639
SUF3INV17 | 69 | CPU running time since system start | SU F3 INV17 | Cpu1UpTime | s | 30.5.3640
SUF3INV17 | 70 | Insulation resistance | SU F3 INV17 | PvGnd_RisIso | kOhm | 30.5.3641
SUF3INV17 | 71 | MV transformer pressure | SU F3 INV17 | PresTrf | "-" | 30.5.3642
SUF3INV17 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV17 | PresTrf_ErrStt | "-" | 30.5.3643
SUF3INV17 | 73 | DC voltage DC plus to DC minus | SU F3 INV17 | DcMs_Vol_F | V | 30.5.3644
SUF3INV17 | 74 | DC current inverter bridge 1 | SU F3 INV17 | DcMs_Amp_Stk1_F | A | 30.5.3645
SUF3INV17 | 75 | DC current inverter bridge 2 | SU F3 INV17 | DcMs_Amp_Stk2_F | A | 30.5.3646
SUF3INV17 | 76 | DC current inverter bridge 3 | SU F3 INV17 | DcMs_Amp_Stk3_F | A | 30.5.3647
SUF3INV17 | 77 | DC current, total | SU F3 INV17 | DcMs_TotAmp_F | A | 30.5.3648
SUF3INV17 | 78 | DC power, total | SU F3 INV17 | DcMs_TotWatt_F | kW | 30.5.3649
SUF3INV17 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV17 | InvMs_DclVol_Stk1_F | V | 30.5.3650
SUF3INV17 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV17 | InvMs_DclVol_Stk2_F | V | 30.5.3651
SUF3INV17 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV17 | InvMs_DclVol_Stk3_F | V | 30.5.3652
SUF3INV17 | 82 | AC current L1, total | SU F3 INV17 | InvMs_TotA_PhsA_F | A | 30.5.3653
SUF3INV17 | 83 | AC current L2, total | SU F3 INV17 | InvMs_TotA_PhsB_F | A | 30.5.3654
SUF3INV17 | 84 | AC current L3, total | SU F3 INV17 | InvMs_TotA_PhsC_F | A | 30.5.3655
SUF3INV17 | 85 | Power factor (cos phi) | SU F3 INV17 | InvMs_PF_F | "-" | 30.5.3656
SUF3INV17 | 86 | Active power, total | SU F3 INV17 | InvMs_TotW_F | kW | 30.5.3657
SUF3INV17 | 87 | Reactive power, total | SU F3 INV17 | InvMs_TotVAr_F | kVAr | 30.5.3658
SUF3INV17 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV17 | GriMs_V_PhsAB_F | V | 30.5.3659
SUF3INV17 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV17 | GriMs_V_PhsBC_F | V | 30.5.3660
SUF3INV17 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV17 | GriMs_V_PhsCA_F | V | 30.5.3661
SUF3INV17 | 91 | Power frequency | SU F3 INV17 | GriMs_Hz_F | Hz | 30.5.3662
SUF3INV17 | 92 | Temperature in the AC range | SU F3 INV17 | TmpCab_Acc_F | °C | 30.5.3663
SUF3INV17 | 93 | Temperature in the DC range | SU F3 INV17 | TmpCab_Dcc_F | °C | 30.5.3664
SUF3INV17 | 94 | Temperature in the electronics area | SU F3 INV17 | TmpCab_Rio_F | °C | 30.5.3665
SUF3INV17 | 95 | Temperature in interior, maximum value | SU F3 INV17 | TmpCab_Max_F | °C | 30.5.3666
SUF3INV17 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV17 | TmpStk_IgbtMax_F | °C | 30.5.3667
SUF3INV17 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV17 | TmpStk_PcbMax_F | °C | 30.5.3668
SUF3INV17 | 98 | Outside temperature | SU F3 INV17 | TmpExl_F | ?C | 30.5.3669
SUF3INV17 | 99 | Temperature of the MV transformer | SU F3 INV17 | TmpTrf_F | °C | 30.5.3670
SUF3INV17 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV17 | TmpStk1_Igbt_F | °C | 30.5.3671
SUF3INV17 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV17 | TmpStk2_Igbt_F | °C | 30.5.3672
SUF3INV17 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV17 | TmpStk3_Igbt_F | °C | 30.5.3673
SUF3INV17 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV17 | TmpStk1_Pcb_F | ?C | 30.5.3674
SUF3INV17 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV17 | TmpStk2_Pcb_F | ?C | 30.5.3675
SUF3INV17 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV17 | TmpStk3_Pcb_F | ?C | 30.5.3676
SUF3INV17 | 106 | MV transformer pressure | SU F3 INV17 | PresTrf_F | "-" | 30.5.3677
SUF3INV17 | 110 | Switching status of the DC load-break switch | SU F3 INV17 | DcSwStt | "-" | 30.5.3678
SUINV17JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV17 | Dat_UpdCnt_1 | "-" | 30.5.3679
SUINV17JB1 | 2 | DC current input 1 | SU F3 INV17 | DcMs_Amp_01 | A | 30.5.3680
SUINV17JB1 | 3 | DC current input 2 | SU F3 INV17 | DcMs_Amp_02 | A | 30.5.3681
SUINV17JB1 | 4 | DC current input 3 | SU F3 INV17 | DcMs_Amp_03 | A | 30.5.3682
SUINV17JB1 | 5 | DC current input 4 | SU F3 INV17 | DcMs_Amp_04 | A | 30.5.3683
SUINV17JB1 | 6 | DC current input 5 | SU F3 INV17 | DcMs_Amp_05 | A | 30.5.3684
SUINV17JB1 | 7 | DC current input 6 | SU F3 INV17 | DcMs_Amp_06 | A | 30.5.3685
SUINV17JB1 | 8 | DC current input 7 | SU F3 INV17 | DcMs_Amp_07 | A | 30.5.3686
SUINV17JB1 | 9 | DC current input 8 | SU F3 INV17 | DcMs_Amp_08 | A | 30.5.3687
SUINV17JB1 | 10 | DC current input 9 | SU F3 INV17 | DcMs_Amp_09 | A | 30.5.3688
SUINV17JB1 | 11 | DC current input 10 | SU F3 INV17 | DcMs_Amp_10 | A | 30.5.3689
SUINV17JB1 | 12 | DC current input 11 | SU F3 INV17 | DcMs_Amp_11 | A | 30.5.3690
SUINV17JB1 | 13 | DC current input 12 | SU F3 INV17 | DcMs_Amp_12 | A | 30.5.3691
SUINV17JB1 | 14 | DC current input 13 | SU F3 INV17 | DcMs_Amp_13 | A | 30.5.3692
SUINV17JB1 | 15 | DC current input 14 | SU F3 INV17 | DcMs_Amp_14 | A | 30.5.3693
SUINV17JB1 | 16 | DC current input 15 | SU F3 INV17 | DcMs_Amp_15 | A | 30.5.3694
SUINV17JB1 | 17 | DC current input 16 | SU F3 INV17 | DcMs_Amp_16 | A | 30.5.3695
SUINV17JB1 | 18 | DC current input 1 | SU F3 INV17 | DcMs_Amp_01_F | A | 30.5.3696
SUINV17JB1 | 19 | DC current input 2 | SU F3 INV17 | DcMs_Amp_02_F | A | 30.5.3697
SUINV17JB1 | 20 | DC current input 3 | SU F3 INV17 | DcMs_Amp_03_F | A | 30.5.3698
SUINV17JB1 | 21 | DC current input 4 | SU F3 INV17 | DcMs_Amp_04_F | A | 30.5.3699
SUINV17JB1 | 22 | DC current input 5 | SU F3 INV17 | DcMs_Amp_05_F | A | 30.5.3700
SUINV17JB1 | 23 | DC current input 6 | SU F3 INV17 | DcMs_Amp_06_F | A | 30.5.3701
SUINV17JB1 | 24 | DC current input 7 | SU F3 INV17 | DcMs_Amp_07_F | A | 30.5.3702
SUINV17JB1 | 25 | DC current input 8 | SU F3 INV17 | DcMs_Amp_08_F | A | 30.5.3703
SUINV17JB1 | 26 | DC current input 9 | SU F3 INV17 | DcMs_Amp_09_F | A | 30.5.3704
SUINV17JB1 | 27 | DC current input 10 | SU F3 INV17 | DcMs_Amp_10_F | A | 30.5.3705
SUINV17JB1 | 28 | DC current input 11 | SU F3 INV17 | DcMs_Amp_11_F | A | 30.5.3706
SUINV17JB1 | 29 | DC current input 12 | SU F3 INV17 | DcMs_Amp_12_F | A | 30.5.3707
SUINV17JB1 | 30 | DC current input 13 | SU F3 INV17 | DcMs_Amp_13_F | A | 30.5.3708
SUINV17JB1 | 31 | DC current input 14 | SU F3 INV17 | DcMs_Amp_14_F | A | 30.5.3709
SUINV17JB1 | 32 | DC current input 15 | SU F3 INV17 | DcMs_Amp_15_F | A | 30.5.3710
SUINV17JB1 | 33 | DC current input 16 | SU F3 INV17 | DcMs_Amp_16_F | A | 30.5.3711
SUINV17JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV17 | Dat_UpdCnt_1 | "-" | 30.5.3712
SUINV17JB2 | 2 | DC current input 1 | SU F3 INV17 | DcMs_Amp_01 | A | 30.5.3713
SUINV17JB2 | 3 | DC current input 2 | SU F3 INV17 | DcMs_Amp_02 | A | 30.5.3714
SUINV17JB2 | 4 | DC current input 3 | SU F3 INV17 | DcMs_Amp_03 | A | 30.5.3715
SUINV17JB2 | 5 | DC current input 4 | SU F3 INV17 | DcMs_Amp_04 | A | 30.5.3716
SUINV17JB2 | 6 | DC current input 5 | SU F3 INV17 | DcMs_Amp_05 | A | 30.5.3717
SUINV17JB2 | 7 | DC current input 6 | SU F3 INV17 | DcMs_Amp_06 | A | 30.5.3718
SUINV17JB2 | 8 | DC current input 7 | SU F3 INV17 | DcMs_Amp_07 | A | 30.5.3719
SUINV17JB2 | 9 | DC current input 8 | SU F3 INV17 | DcMs_Amp_08 | A | 30.5.3720
SUINV17JB2 | 10 | DC current input 9 | SU F3 INV17 | DcMs_Amp_09 | A | 30.5.3721
SUINV17JB2 | 11 | DC current input 10 | SU F3 INV17 | DcMs_Amp_10 | A | 30.5.3722
SUINV17JB2 | 12 | DC current input 11 | SU F3 INV17 | DcMs_Amp_11 | A | 30.5.3723
SUINV17JB2 | 13 | DC current input 12 | SU F3 INV17 | DcMs_Amp_12 | A | 30.5.3724
SUINV17JB2 | 14 | DC current input 13 | SU F3 INV17 | DcMs_Amp_13 | A | 30.5.3725
SUINV17JB2 | 15 | DC current input 14 | SU F3 INV17 | DcMs_Amp_14 | A | 30.5.3726
SUINV17JB2 | 16 | DC current input 15 | SU F3 INV17 | DcMs_Amp_15 | A | 30.5.3727
SUINV17JB2 | 17 | DC current input 16 | SU F3 INV17 | DcMs_Amp_16 | A | 30.5.3728
SUINV17JB2 | 18 | DC current input 1 | SU F3 INV17 | DcMs_Amp_01_F | A | 30.5.3729
SUINV17JB2 | 19 | DC current input 2 | SU F3 INV17 | DcMs_Amp_02_F | A | 30.5.3730
SUINV17JB2 | 20 | DC current input 3 | SU F3 INV17 | DcMs_Amp_03_F | A | 30.5.3731
SUINV17JB2 | 21 | DC current input 4 | SU F3 INV17 | DcMs_Amp_04_F | A | 30.5.3732
SUINV17JB2 | 22 | DC current input 5 | SU F3 INV17 | DcMs_Amp_05_F | A | 30.5.3733
SUINV17JB2 | 23 | DC current input 6 | SU F3 INV17 | DcMs_Amp_06_F | A | 30.5.3734
SUINV17JB2 | 24 | DC current input 7 | SU F3 INV17 | DcMs_Amp_07_F | A | 30.5.3735
SUINV17JB2 | 25 | DC current input 8 | SU F3 INV17 | DcMs_Amp_08_F | A | 30.5.3736
SUINV17JB2 | 26 | DC current input 9 | SU F3 INV17 | DcMs_Amp_09_F | A | 30.5.3737
SUINV17JB2 | 27 | DC current input 10 | SU F3 INV17 | DcMs_Amp_10_F | A | 30.5.3738
SUINV17JB2 | 28 | DC current input 11 | SU F3 INV17 | DcMs_Amp_11_F | A | 30.5.3739
SUINV17JB2 | 29 | DC current input 12 | SU F3 INV17 | DcMs_Amp_12_F | A | 30.5.3740
SUINV17JB2 | 30 | DC current input 13 | SU F3 INV17 | DcMs_Amp_13_F | A | 30.5.3741
SUINV17JB2 | 31 | DC current input 14 | SU F3 INV17 | DcMs_Amp_14_F | A | 30.5.3742
SUINV17JB2 | 32 | DC current input 15 | SU F3 INV17 | DcMs_Amp_15_F | A | 30.5.3743
SUINV17JB2 | 33 | DC current input 16 | SU F3 INV17 | DcMs_Amp_16_F | A | 30.5.3744
SUF3INV18 | 1 | DC voltage DC plus to DC minus | SU F3 INV18 | DcMs_Vol | V | 30.5.3745
SUF3INV18 | 2 | DC current inverter bridge 1 | SU F3 INV18 | DcMs_Amp_Stk1 | A | 30.5.3746
SUF3INV18 | 3 | DC current inverter bridge 2 | SU F3 INV18 | DcMs_Amp_Stk2 | A | 30.5.3747
SUF3INV18 | 4 | DC current inverter bridge 3 | SU F3 INV18 | DcMs_Amp_Stk3 | A | 30.5.3748
SUF3INV18 | 5 | DC current, total | SU F3 INV18 | DcMs_TotAmp | A | 30.5.3749
SUF3INV18 | 6 | DC power, total | SU F3 INV18 | DcMs_TotWatt | kW | 30.5.3750
SUF3INV18 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV18 | InvMs_DclVol_Stk1 | V | 30.5.3751
SUF3INV18 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV18 | InvMs_DclVol_Stk2 | V | 30.5.3752
SUF3INV18 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV18 | InvMs_DclVol_Stk3 | V | 30.5.3753
SUF3INV18 | 10 | AC current L1, total | SU F3 INV18 | InvMs_TotA_PhsA | A | 30.5.3754
SUF3INV18 | 11 | AC current L2, total | SU F3 INV18 | InvMs_TotA_PhsB | A | 30.5.3755
SUF3INV18 | 12 | AC current L3, total | SU F3 INV18 | InvMs_TotA_PhsC | A | 30.5.3756
SUF3INV18 | 13 | Power factor (cos phi) | SU F3 INV18 | InvMs_PF | "-" | 30.5.3757
SUF3INV18 | 14 | Apparent power, total | SU F3 INV18 | InvMs_TotVA | kVA | 30.5.3758
SUF3INV18 | 15 | Active power, total | SU F3 INV18 | InvMs_TotW | kW | 30.5.3759
SUF3INV18 | 16 | Reactive power, total | SU F3 INV18 | InvMs_TotVAr | kVAr | 30.5.3760
SUF3INV18 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV18 | GriMs_V_PhsAB | V | 30.5.3761
SUF3INV18 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV18 | GriMs_V_PhsBC | V | 30.5.3762
SUF3INV18 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV18 | GriMs_V_PhsCA | V | 30.5.3763
SUF3INV18 | 20 | Power frequency | SU F3 INV18 | GriMs_Hz | Hz | 30.5.3764
SUF3INV18 | 21 | Temperature in the AC range | SU F3 INV18 | TmpCab_Acc | °C | 30.5.3765
SUF3INV18 | 22 | Temperature in the DC range | SU F3 INV18 | TmpCab_Dcc | °C | 30.5.3766
SUF3INV18 | 23 | Temperature in the electronics area | SU F3 INV18 | TmpCab_Rio | °C | 30.5.3767
SUF3INV18 | 24 | Temperature in interior, maximum value | SU F3 INV18 | TmpCab_Max | °C | 30.5.3768
SUF3INV18 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV18 | TmpStk_IgbtMax | °C | 30.5.3769
SUF3INV18 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV18 | TmpStk_PcbMax | °C | 30.5.3770
SUF3INV18 | 27 | Outside temperature | SU F3 INV18 | TmpExl | ?C | 30.5.3771
SUF3INV18 | 28 | Temperature of the MV transformer | SU F3 INV18 | TmpTrf | °C | 30.5.3772
SUF3INV18 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV18 | DcSw1Stt | "-" | 30.5.3773
SUF3INV18 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV18 | DcSw2Stt | "-" | 30.5.3774
SUF3INV18 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV18 | DcSw3Stt | "-" | 30.5.3775
SUF3INV18 | 32 | Switching status of the AC circuit breaker | SU F3 INV18 | AcSwStt | "-" | 30.5.3776
SUF3INV18 | 33 | Switching state of the capacitor contactor | SU F3 INV18 | CapacSwStt | "-" | 30.5.3777
SUF3INV18 | 34 | Switching status of the pre-charging contactor | SU F3 INV18 | PrchrgSwStt | "-" | 30.5.3778
SUF3INV18 | 35 | Feed-in hours | SU F3 INV18 | Cnt_TotFeedTm | "-" | 30.5.3779
SUF3INV18 | 36 | Operating hours | SU F3 INV18 | Cnt_TotOpTm | "-" | 30.5.3780
SUF3INV18 | 37 | DC energy drawn, total | SU F3 INV18 | Cnt_TotWatthIn | MWh | 30.5.3781
SUF3INV18 | 38 | AC energy fed in, total | SU F3 INV18 | Cnt_TotWhOut | MWh | 30.5.3782
SUF3INV18 | 39 | DC energy drawn that day | SU F3 INV18 | Cnt_WatthIn | MWh | 30.5.3783
SUF3INV18 | 40 | AC energy fed in that day | SU F3 INV18 | Cnt_WhOut | MWh | 30.5.3784
SUF3INV18 | 41 | Operating hours of the interior fan 1 | SU F3 INV18 | Cnt_FanCab1Tm | "-" | 30.5.3785
SUF3INV18 | 42 | Operating hours of the interior fan 2 | SU F3 INV18 | Cnt_FanCab2Tm | "-" | 30.5.3786
SUF3INV18 | 43 | Operating hours of the inverter bridge fan | SU F3 INV18 | Cnt_FanStkTm | "-" | 30.5.3787
SUF3INV18 | 44 | Operating hours of the internal heating element | SU F3 INV18 | Cnt_HtCabTm | "-" | 30.5.3788
SUF3INV18 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV18 | Cnt_HtLoExlTmpTm | "-" | 30.5.3789
SUF3INV18 | 46 | Error location of the present error | SU F3 INV18 | ErrLcn | "-" | 30.5.3790
SUF3INV18 | 47 | Error status of the inverter | SU F3 INV18 | ErrStt | "-" | 30.5.3791
SUF3INV18 | 48 | Error number of the present error | SU F3 INV18 | ErrNo | "-" | 30.5.3792
SUF3INV18 | 49 | Operating state of the inverter | SU F3 INV18 | OpStt | "-" | 30.5.3793
SUF3INV18 | 50 | Switch status of the start-stop key switch | SU F3 INV18 | Rio_KeySw | "-" | 30.5.3794
SUF3INV18 | 51 | Waiting time for grid connection | SU F3 INV18 | WaitGriTm | s | 30.5.3795
SUF3INV18 | 52 | Inverter serial number | SU F3 INV18 | DevInf_SerNo | "-" | 30.5.3796
SUF3INV18 | 53 | Switching status of the GFDI | SU F3 INV18 | GfdiSwStt | "-" | 30.5.3797
SUF3INV18 | 54 | Active power, setpoint | SU F3 INV18 | WSpt | kW | 30.5.3798
SUF3INV18 | 55 | Maximum apparent power, setpoint | SU F3 INV18 | VAMaxSpt | kVA | 30.5.3799
SUF3INV18 | 56 | Reactive power, setpoint | SU F3 INV18 | VArSpt | kVAr | 30.5.3800
SUF3INV18 | 57 | Power factor cos (phi), setpoint | SU F3 INV18 | PFSpt | "-" | 30.5.3801
SUF3INV18 | 58 | Fast stop hermetic protection, pressure | SU F3 INV18 | TrfPro_Pres | "-" | 30.5.3802
SUF3INV18 | 59 | Fast stop hermetic protection, temperature | SU F3 INV18 | TrfPro_TmpTrp | "-" | 30.5.3803
SUF3INV18 | 60 | Hermetic protection, gas fill level | SU F3 INV18 | TrfPro_GasOilLev | "-" | 30.5.3804
SUF3INV18 | 61 | Hermetic pressure, temperature warning | SU F3 INV18 | TrfPro_TmpWrn | "-" | 30.5.3805
SUF3INV18 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV18 | TmpStk1_Igbt | °C | 30.5.3806
SUF3INV18 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV18 | TmpStk2_Igbt | °C | 30.5.3807
SUF3INV18 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV18 | TmpStk3_Igbt | °C | 30.5.3808
SUF3INV18 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV18 | TmpStk1_Pcb | ?C | 30.5.3809
SUF3INV18 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV18 | TmpStk2_Pcb | ?C | 30.5.3810
SUF3INV18 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV18 | TmpStk3_Pcb | ?C | 30.5.3811
SUF3INV18 | 68 | AC Energy Fed in the previous Day | SU F3 INV18 | Cnt_YstdWhOut | MWh | 30.5.3812
SUF3INV18 | 69 | CPU running time since system start | SU F3 INV18 | Cpu1UpTime | s | 30.5.3813
SUF3INV18 | 70 | Insulation resistance | SU F3 INV18 | PvGnd_RisIso | kOhm | 30.5.3814
SUF3INV18 | 71 | MV transformer pressure | SU F3 INV18 | PresTrf | "-" | 30.5.3815
SUF3INV18 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV18 | PresTrf_ErrStt | "-" | 30.5.3816
SUF3INV18 | 73 | DC voltage DC plus to DC minus | SU F3 INV18 | DcMs_Vol_F | V | 30.5.3817
SUF3INV18 | 74 | DC current inverter bridge 1 | SU F3 INV18 | DcMs_Amp_Stk1_F | A | 30.5.3818
SUF3INV18 | 75 | DC current inverter bridge 2 | SU F3 INV18 | DcMs_Amp_Stk2_F | A | 30.5.3819
SUF3INV18 | 76 | DC current inverter bridge 3 | SU F3 INV18 | DcMs_Amp_Stk3_F | A | 30.5.3820
SUF3INV18 | 77 | DC current, total | SU F3 INV18 | DcMs_TotAmp_F | A | 30.5.3821
SUF3INV18 | 78 | DC power, total | SU F3 INV18 | DcMs_TotWatt_F | kW | 30.5.3822
SUF3INV18 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV18 | InvMs_DclVol_Stk1_F | V | 30.5.3823
SUF3INV18 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV18 | InvMs_DclVol_Stk2_F | V | 30.5.3824
SUF3INV18 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV18 | InvMs_DclVol_Stk3_F | V | 30.5.3825
SUF3INV18 | 82 | AC current L1, total | SU F3 INV18 | InvMs_TotA_PhsA_F | A | 30.5.3826
SUF3INV18 | 83 | AC current L2, total | SU F3 INV18 | InvMs_TotA_PhsB_F | A | 30.5.3827
SUF3INV18 | 84 | AC current L3, total | SU F3 INV18 | InvMs_TotA_PhsC_F | A | 30.5.3828
SUF3INV18 | 85 | Power factor (cos phi) | SU F3 INV18 | InvMs_PF_F | "-" | 30.5.3829
SUF3INV18 | 86 | Active power, total | SU F3 INV18 | InvMs_TotW_F | kW | 30.5.3830
SUF3INV18 | 87 | Reactive power, total | SU F3 INV18 | InvMs_TotVAr_F | kVAr | 30.5.3831
SUF3INV18 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV18 | GriMs_V_PhsAB_F | V | 30.5.3832
SUF3INV18 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV18 | GriMs_V_PhsBC_F | V | 30.5.3833
SUF3INV18 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV18 | GriMs_V_PhsCA_F | V | 30.5.3834
SUF3INV18 | 91 | Power frequency | SU F3 INV18 | GriMs_Hz_F | Hz | 30.5.3835
SUF3INV18 | 92 | Temperature in the AC range | SU F3 INV18 | TmpCab_Acc_F | °C | 30.5.3836
SUF3INV18 | 93 | Temperature in the DC range | SU F3 INV18 | TmpCab_Dcc_F | °C | 30.5.3837
SUF3INV18 | 94 | Temperature in the electronics area | SU F3 INV18 | TmpCab_Rio_F | °C | 30.5.3838
SUF3INV18 | 95 | Temperature in interior, maximum value | SU F3 INV18 | TmpCab_Max_F | °C | 30.5.3839
SUF3INV18 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV18 | TmpStk_IgbtMax_F | °C | 30.5.3840
SUF3INV18 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV18 | TmpStk_PcbMax_F | °C | 30.5.3841
SUF3INV18 | 98 | Outside temperature | SU F3 INV18 | TmpExl_F | ?C | 30.5.3842
SUF3INV18 | 99 | Temperature of the MV transformer | SU F3 INV18 | TmpTrf_F | °C | 30.5.3843
SUF3INV18 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV18 | TmpStk1_Igbt_F | °C | 30.5.3844
SUF3INV18 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV18 | TmpStk2_Igbt_F | °C | 30.5.3845
SUF3INV18 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV18 | TmpStk3_Igbt_F | °C | 30.5.3846
SUF3INV18 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV18 | TmpStk1_Pcb_F | ?C | 30.5.3847
SUF3INV18 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV18 | TmpStk2_Pcb_F | ?C | 30.5.3848
SUF3INV18 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV18 | TmpStk3_Pcb_F | ?C | 30.5.3849
SUF3INV18 | 106 | MV transformer pressure | SU F3 INV18 | PresTrf_F | "-" | 30.5.3850
SUF3INV18 | 110 | Switching status of the DC load-break switch | SU F3 INV18 | DcSwStt | "-" | 30.5.3851
SUINV18JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV18 | Dat_UpdCnt_1 | "-" | 30.5.3852
SUINV18JB1 | 2 | DC current input 1 | SU F3 INV18 | DcMs_Amp_01 | A | 30.5.3853
SUINV18JB1 | 3 | DC current input 2 | SU F3 INV18 | DcMs_Amp_02 | A | 30.5.3854
SUINV18JB1 | 4 | DC current input 3 | SU F3 INV18 | DcMs_Amp_03 | A | 30.5.3855
SUINV18JB1 | 5 | DC current input 4 | SU F3 INV18 | DcMs_Amp_04 | A | 30.5.3856
SUINV18JB1 | 6 | DC current input 5 | SU F3 INV18 | DcMs_Amp_05 | A | 30.5.3857
SUINV18JB1 | 7 | DC current input 6 | SU F3 INV18 | DcMs_Amp_06 | A | 30.5.3858
SUINV18JB1 | 8 | DC current input 7 | SU F3 INV18 | DcMs_Amp_07 | A | 30.5.3859
SUINV18JB1 | 9 | DC current input 8 | SU F3 INV18 | DcMs_Amp_08 | A | 30.5.3860
SUINV18JB1 | 10 | DC current input 9 | SU F3 INV18 | DcMs_Amp_09 | A | 30.5.3861
SUINV18JB1 | 11 | DC current input 10 | SU F3 INV18 | DcMs_Amp_10 | A | 30.5.3862
SUINV18JB1 | 12 | DC current input 11 | SU F3 INV18 | DcMs_Amp_11 | A | 30.5.3863
SUINV18JB1 | 13 | DC current input 12 | SU F3 INV18 | DcMs_Amp_12 | A | 30.5.3864
SUINV18JB1 | 14 | DC current input 13 | SU F3 INV18 | DcMs_Amp_13 | A | 30.5.3865
SUINV18JB1 | 15 | DC current input 14 | SU F3 INV18 | DcMs_Amp_14 | A | 30.5.3866
SUINV18JB1 | 16 | DC current input 15 | SU F3 INV18 | DcMs_Amp_15 | A | 30.5.3867
SUINV18JB1 | 17 | DC current input 16 | SU F3 INV18 | DcMs_Amp_16 | A | 30.5.3868
SUINV18JB1 | 18 | DC current input 1 | SU F3 INV18 | DcMs_Amp_01_F | A | 30.5.3869
SUINV18JB1 | 19 | DC current input 2 | SU F3 INV18 | DcMs_Amp_02_F | A | 30.5.3870
SUINV18JB1 | 20 | DC current input 3 | SU F3 INV18 | DcMs_Amp_03_F | A | 30.5.3871
SUINV18JB1 | 21 | DC current input 4 | SU F3 INV18 | DcMs_Amp_04_F | A | 30.5.3872
SUINV18JB1 | 22 | DC current input 5 | SU F3 INV18 | DcMs_Amp_05_F | A | 30.5.3873
SUINV18JB1 | 23 | DC current input 6 | SU F3 INV18 | DcMs_Amp_06_F | A | 30.5.3874
SUINV18JB1 | 24 | DC current input 7 | SU F3 INV18 | DcMs_Amp_07_F | A | 30.5.3875
SUINV18JB1 | 25 | DC current input 8 | SU F3 INV18 | DcMs_Amp_08_F | A | 30.5.3876
SUINV18JB1 | 26 | DC current input 9 | SU F3 INV18 | DcMs_Amp_09_F | A | 30.5.3877
SUINV18JB1 | 27 | DC current input 10 | SU F3 INV18 | DcMs_Amp_10_F | A | 30.5.3878
SUINV18JB1 | 28 | DC current input 11 | SU F3 INV18 | DcMs_Amp_11_F | A | 30.5.3879
SUINV18JB1 | 29 | DC current input 12 | SU F3 INV18 | DcMs_Amp_12_F | A | 30.5.3880
SUINV18JB1 | 30 | DC current input 13 | SU F3 INV18 | DcMs_Amp_13_F | A | 30.5.3881
SUINV18JB1 | 31 | DC current input 14 | SU F3 INV18 | DcMs_Amp_14_F | A | 30.5.3882
SUINV18JB1 | 32 | DC current input 15 | SU F3 INV18 | DcMs_Amp_15_F | A | 30.5.3883
SUINV18JB1 | 33 | DC current input 16 | SU F3 INV18 | DcMs_Amp_16_F | A | 30.5.3884
SUINV18JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV18 | Dat_UpdCnt_1 | "-" | 30.5.3885
SUINV18JB2 | 2 | DC current input 1 | SU F3 INV18 | DcMs_Amp_01 | A | 30.5.3886
SUINV18JB2 | 3 | DC current input 2 | SU F3 INV18 | DcMs_Amp_02 | A | 30.5.3887
SUINV18JB2 | 4 | DC current input 3 | SU F3 INV18 | DcMs_Amp_03 | A | 30.5.3888
SUINV18JB2 | 5 | DC current input 4 | SU F3 INV18 | DcMs_Amp_04 | A | 30.5.3889
SUINV18JB2 | 6 | DC current input 5 | SU F3 INV18 | DcMs_Amp_05 | A | 30.5.3890
SUINV18JB2 | 7 | DC current input 6 | SU F3 INV18 | DcMs_Amp_06 | A | 30.5.3891
SUINV18JB2 | 8 | DC current input 7 | SU F3 INV18 | DcMs_Amp_07 | A | 30.5.3892
SUINV18JB2 | 9 | DC current input 8 | SU F3 INV18 | DcMs_Amp_08 | A | 30.5.3893
SUINV18JB2 | 10 | DC current input 9 | SU F3 INV18 | DcMs_Amp_09 | A | 30.5.3894
SUINV18JB2 | 11 | DC current input 10 | SU F3 INV18 | DcMs_Amp_10 | A | 30.5.3895
SUINV18JB2 | 12 | DC current input 11 | SU F3 INV18 | DcMs_Amp_11 | A | 30.5.3896
SUINV18JB2 | 13 | DC current input 12 | SU F3 INV18 | DcMs_Amp_12 | A | 30.5.3897
SUINV18JB2 | 14 | DC current input 13 | SU F3 INV18 | DcMs_Amp_13 | A | 30.5.3898
SUINV18JB2 | 15 | DC current input 14 | SU F3 INV18 | DcMs_Amp_14 | A | 30.5.3899
SUINV18JB2 | 16 | DC current input 15 | SU F3 INV18 | DcMs_Amp_15 | A | 30.5.3900
SUINV18JB2 | 17 | DC current input 16 | SU F3 INV18 | DcMs_Amp_16 | A | 30.5.3901
SUINV18JB2 | 18 | DC current input 1 | SU F3 INV18 | DcMs_Amp_01_F | A | 30.5.3902
SUINV18JB2 | 19 | DC current input 2 | SU F3 INV18 | DcMs_Amp_02_F | A | 30.5.3903
SUINV18JB2 | 20 | DC current input 3 | SU F3 INV18 | DcMs_Amp_03_F | A | 30.5.3904
SUINV18JB2 | 21 | DC current input 4 | SU F3 INV18 | DcMs_Amp_04_F | A | 30.5.3905
SUINV18JB2 | 22 | DC current input 5 | SU F3 INV18 | DcMs_Amp_05_F | A | 30.5.3906
SUINV18JB2 | 23 | DC current input 6 | SU F3 INV18 | DcMs_Amp_06_F | A | 30.5.3907
SUINV18JB2 | 24 | DC current input 7 | SU F3 INV18 | DcMs_Amp_07_F | A | 30.5.3908
SUINV18JB2 | 25 | DC current input 8 | SU F3 INV18 | DcMs_Amp_08_F | A | 30.5.3909
SUINV18JB2 | 26 | DC current input 9 | SU F3 INV18 | DcMs_Amp_09_F | A | 30.5.3910
SUINV18JB2 | 27 | DC current input 10 | SU F3 INV18 | DcMs_Amp_10_F | A | 30.5.3911
SUINV18JB2 | 28 | DC current input 11 | SU F3 INV18 | DcMs_Amp_11_F | A | 30.5.3912
SUINV18JB2 | 29 | DC current input 12 | SU F3 INV18 | DcMs_Amp_12_F | A | 30.5.3913
SUINV18JB2 | 30 | DC current input 13 | SU F3 INV18 | DcMs_Amp_13_F | A | 30.5.3914
SUINV18JB2 | 31 | DC current input 14 | SU F3 INV18 | DcMs_Amp_14_F | A | 30.5.3915
SUINV18JB2 | 32 | DC current input 15 | SU F3 INV18 | DcMs_Amp_15_F | A | 30.5.3916
SUINV18JB2 | 33 | DC current input 16 | SU F3 INV18 | DcMs_Amp_16_F | A | 30.5.3917
SUF3INV20 | 1 | DC voltage DC plus to DC minus | SU F3 INV20 | DcMs_Vol | V | 30.5.3918
SUF3INV20 | 2 | DC current inverter bridge 1 | SU F3 INV20 | DcMs_Amp_Stk1 | A | 30.5.3919
SUF3INV20 | 3 | DC current inverter bridge 2 | SU F3 INV20 | DcMs_Amp_Stk2 | A | 30.5.3920
SUF3INV20 | 4 | DC current inverter bridge 3 | SU F3 INV20 | DcMs_Amp_Stk3 | A | 30.5.3921
SUF3INV20 | 5 | DC current, total | SU F3 INV20 | DcMs_TotAmp | A | 30.5.3922
SUF3INV20 | 6 | DC power, total | SU F3 INV20 | DcMs_TotWatt | kW | 30.5.3923
SUF3INV20 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV20 | InvMs_DclVol_Stk1 | V | 30.5.3924
SUF3INV20 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV20 | InvMs_DclVol_Stk2 | V | 30.5.3925
SUF3INV20 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV20 | InvMs_DclVol_Stk3 | V | 30.5.3926
SUF3INV20 | 10 | AC current L1, total | SU F3 INV20 | InvMs_TotA_PhsA | A | 30.5.3927
SUF3INV20 | 11 | AC current L2, total | SU F3 INV20 | InvMs_TotA_PhsB | A | 30.5.3928
SUF3INV20 | 12 | AC current L3, total | SU F3 INV20 | InvMs_TotA_PhsC | A | 30.5.3929
SUF3INV20 | 13 | Power factor (cos phi) | SU F3 INV20 | InvMs_PF | "-" | 30.5.3930
SUF3INV20 | 14 | Apparent power, total | SU F3 INV20 | InvMs_TotVA | kVA | 30.5.3931
SUF3INV20 | 15 | Active power, total | SU F3 INV20 | InvMs_TotW | kW | 30.5.3932
SUF3INV20 | 16 | Reactive power, total | SU F3 INV20 | InvMs_TotVAr | kVAr | 30.5.3933
SUF3INV20 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV20 | GriMs_V_PhsAB | V | 30.5.3934
SUF3INV20 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV20 | GriMs_V_PhsBC | V | 30.5.3935
SUF3INV20 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV20 | GriMs_V_PhsCA | V | 30.5.3936
SUF3INV20 | 20 | Power frequency | SU F3 INV20 | GriMs_Hz | Hz | 30.5.3937
SUF3INV20 | 21 | Temperature in the AC range | SU F3 INV20 | TmpCab_Acc | °C | 30.5.3938
SUF3INV20 | 22 | Temperature in the DC range | SU F3 INV20 | TmpCab_Dcc | °C | 30.5.3939
SUF3INV20 | 23 | Temperature in the electronics area | SU F3 INV20 | TmpCab_Rio | °C | 30.5.3940
SUF3INV20 | 24 | Temperature in interior, maximum value | SU F3 INV20 | TmpCab_Max | °C | 30.5.3941
SUF3INV20 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV20 | TmpStk_IgbtMax | °C | 30.5.3942
SUF3INV20 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV20 | TmpStk_PcbMax | °C | 30.5.3943
SUF3INV20 | 27 | Outside temperature | SU F3 INV20 | TmpExl | ?C | 30.5.3944
SUF3INV20 | 28 | Temperature of the MV transformer | SU F3 INV20 | TmpTrf | °C | 30.5.3945
SUF3INV20 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV20 | DcSw1Stt | "-" | 30.5.3946
SUF3INV20 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV20 | DcSw2Stt | "-" | 30.5.3947
SUF3INV20 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV20 | DcSw3Stt | "-" | 30.5.3948
SUF3INV20 | 32 | Switching status of the AC circuit breaker | SU F3 INV20 | AcSwStt | "-" | 30.5.3949
SUF3INV20 | 33 | Switching state of the capacitor contactor | SU F3 INV20 | CapacSwStt | "-" | 30.5.3950
SUF3INV20 | 34 | Switching status of the pre-charging contactor | SU F3 INV20 | PrchrgSwStt | "-" | 30.5.3951
SUF3INV20 | 35 | Feed-in hours | SU F3 INV20 | Cnt_TotFeedTm | "-" | 30.5.3952
SUF3INV20 | 36 | Operating hours | SU F3 INV20 | Cnt_TotOpTm | "-" | 30.5.3953
SUF3INV20 | 37 | DC energy drawn, total | SU F3 INV20 | Cnt_TotWatthIn | MWh | 30.5.3954
SUF3INV20 | 38 | AC energy fed in, total | SU F3 INV20 | Cnt_TotWhOut | MWh | 30.5.3955
SUF3INV20 | 39 | DC energy drawn that day | SU F3 INV20 | Cnt_WatthIn | MWh | 30.5.3956
SUF3INV20 | 40 | AC energy fed in that day | SU F3 INV20 | Cnt_WhOut | MWh | 30.5.3957
SUF3INV20 | 41 | Operating hours of the interior fan 1 | SU F3 INV20 | Cnt_FanCab1Tm | "-" | 30.5.3958
SUF3INV20 | 42 | Operating hours of the interior fan 2 | SU F3 INV20 | Cnt_FanCab2Tm | "-" | 30.5.3959
SUF3INV20 | 43 | Operating hours of the inverter bridge fan | SU F3 INV20 | Cnt_FanStkTm | "-" | 30.5.3960
SUF3INV20 | 44 | Operating hours of the internal heating element | SU F3 INV20 | Cnt_HtCabTm | "-" | 30.5.3961
SUF3INV20 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV20 | Cnt_HtLoExlTmpTm | "-" | 30.5.3962
SUF3INV20 | 46 | Error location of the present error | SU F3 INV20 | ErrLcn | "-" | 30.5.3963
SUF3INV20 | 47 | Error status of the inverter | SU F3 INV20 | ErrStt | "-" | 30.5.3964
SUF3INV20 | 48 | Error number of the present error | SU F3 INV20 | ErrNo | "-" | 30.5.3965
SUF3INV20 | 49 | Operating state of the inverter | SU F3 INV20 | OpStt | "-" | 30.5.3966
SUF3INV20 | 50 | Switch status of the start-stop key switch | SU F3 INV20 | Rio_KeySw | "-" | 30.5.3967
SUF3INV20 | 51 | Waiting time for grid connection | SU F3 INV20 | WaitGriTm | s | 30.5.3968
SUF3INV20 | 52 | Inverter serial number | SU F3 INV20 | DevInf_SerNo | "-" | 30.5.3969
SUF3INV20 | 53 | Switching status of the GFDI | SU F3 INV20 | GfdiSwStt | "-" | 30.5.3970
SUF3INV20 | 54 | Active power, setpoint | SU F3 INV20 | WSpt | kW | 30.5.3971
SUF3INV20 | 55 | Maximum apparent power, setpoint | SU F3 INV20 | VAMaxSpt | kVA | 30.5.3972
SUF3INV20 | 56 | Reactive power, setpoint | SU F3 INV20 | VArSpt | kVAr | 30.5.3973
SUF3INV20 | 57 | Power factor cos (phi), setpoint | SU F3 INV20 | PFSpt | "-" | 30.5.3974
SUF3INV20 | 58 | Fast stop hermetic protection, pressure | SU F3 INV20 | TrfPro_Pres | "-" | 30.5.3975
SUF3INV20 | 59 | Fast stop hermetic protection, temperature | SU F3 INV20 | TrfPro_TmpTrp | "-" | 30.5.3976
SUF3INV20 | 60 | Hermetic protection, gas fill level | SU F3 INV20 | TrfPro_GasOilLev | "-" | 30.5.3977
SUF3INV20 | 61 | Hermetic pressure, temperature warning | SU F3 INV20 | TrfPro_TmpWrn | "-" | 30.5.3978
SUF3INV20 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV20 | TmpStk1_Igbt | °C | 30.5.3979
SUF3INV20 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV20 | TmpStk2_Igbt | °C | 30.5.3980
SUF3INV20 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV20 | TmpStk3_Igbt | °C | 30.5.3981
SUF3INV20 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV20 | TmpStk1_Pcb | ?C | 30.5.3982
SUF3INV20 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV20 | TmpStk2_Pcb | ?C | 30.5.3983
SUF3INV20 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV20 | TmpStk3_Pcb | ?C | 30.5.3984
SUF3INV20 | 68 | AC Energy Fed in the previous Day | SU F3 INV20 | Cnt_YstdWhOut | MWh | 30.5.3985
SUF3INV20 | 69 | CPU running time since system start | SU F3 INV20 | Cpu1UpTime | s | 30.5.3986
SUF3INV20 | 70 | Insulation resistance | SU F3 INV20 | PvGnd_RisIso | kOhm | 30.5.3987
SUF3INV20 | 71 | MV transformer pressure | SU F3 INV20 | PresTrf | "-" | 30.5.3988
SUF3INV20 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV20 | PresTrf_ErrStt | "-" | 30.5.3989
SUF3INV20 | 73 | DC voltage DC plus to DC minus | SU F3 INV20 | DcMs_Vol_F | V | 30.5.3990
SUF3INV20 | 74 | DC current inverter bridge 1 | SU F3 INV20 | DcMs_Amp_Stk1_F | A | 30.5.3991
SUF3INV20 | 75 | DC current inverter bridge 2 | SU F3 INV20 | DcMs_Amp_Stk2_F | A | 30.5.3992
SUF3INV20 | 76 | DC current inverter bridge 3 | SU F3 INV20 | DcMs_Amp_Stk3_F | A | 30.5.3993
SUF3INV20 | 77 | DC current, total | SU F3 INV20 | DcMs_TotAmp_F | A | 30.5.3994
SUF3INV20 | 78 | DC power, total | SU F3 INV20 | DcMs_TotWatt_F | kW | 30.5.3995
SUF3INV20 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV20 | InvMs_DclVol_Stk1_F | V | 30.5.3996
SUF3INV20 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV20 | InvMs_DclVol_Stk2_F | V | 30.5.3997
SUF3INV20 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV20 | InvMs_DclVol_Stk3_F | V | 30.5.3998
SUF3INV20 | 82 | AC current L1, total | SU F3 INV20 | InvMs_TotA_PhsA_F | A | 30.5.3999
SUF3INV20 | 83 | AC current L2, total | SU F3 INV20 | InvMs_TotA_PhsB_F | A | 30.5.4000
SUF3INV20 | 84 | AC current L3, total | SU F3 INV20 | InvMs_TotA_PhsC_F | A | 30.5.4001
SUF3INV20 | 85 | Power factor (cos phi) | SU F3 INV20 | InvMs_PF_F | "-" | 30.5.4002
SUF3INV20 | 86 | Active power, total | SU F3 INV20 | InvMs_TotW_F | kW | 30.5.4003
SUF3INV20 | 87 | Reactive power, total | SU F3 INV20 | InvMs_TotVAr_F | kVAr | 30.5.4004
SUF3INV20 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV20 | GriMs_V_PhsAB_F | V | 30.5.4005
SUF3INV20 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV20 | GriMs_V_PhsBC_F | V | 30.5.4006
SUF3INV20 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV20 | GriMs_V_PhsCA_F | V | 30.5.4007
SUF3INV20 | 91 | Power frequency | SU F3 INV20 | GriMs_Hz_F | Hz | 30.5.4008
SUF3INV20 | 92 | Temperature in the AC range | SU F3 INV20 | TmpCab_Acc_F | °C | 30.5.4009
SUF3INV20 | 93 | Temperature in the DC range | SU F3 INV20 | TmpCab_Dcc_F | °C | 30.5.4010
SUF3INV20 | 94 | Temperature in the electronics area | SU F3 INV20 | TmpCab_Rio_F | °C | 30.5.4011
SUF3INV20 | 95 | Temperature in interior, maximum value | SU F3 INV20 | TmpCab_Max_F | °C | 30.5.4012
SUF3INV20 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV20 | TmpStk_IgbtMax_F | °C | 30.5.4013
SUF3INV20 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV20 | TmpStk_PcbMax_F | °C | 30.5.4014
SUF3INV20 | 98 | Outside temperature | SU F3 INV20 | TmpExl_F | ?C | 30.5.4015
SUF3INV20 | 99 | Temperature of the MV transformer | SU F3 INV20 | TmpTrf_F | °C | 30.5.4016
SUF3INV20 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV20 | TmpStk1_Igbt_F | °C | 30.5.4017
SUF3INV20 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV20 | TmpStk2_Igbt_F | °C | 30.5.4018
SUF3INV20 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV20 | TmpStk3_Igbt_F | °C | 30.5.4019
SUF3INV20 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV20 | TmpStk1_Pcb_F | ?C | 30.5.4020
SUF3INV20 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV20 | TmpStk2_Pcb_F | ?C | 30.5.4021
SUF3INV20 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV20 | TmpStk3_Pcb_F | ?C | 30.5.4022
SUF3INV20 | 106 | MV transformer pressure | SU F3 INV20 | PresTrf_F | "-" | 30.5.4023
SUF3INV20 | 110 | Switching status of the DC load-break switch | SU F3 INV20 | DcSwStt | "-" | 30.5.4024
SUINV20JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV20 | Dat_UpdCnt_1 | "-" | 30.5.4025
SUINV20JB1 | 2 | DC current input 1 | SU F3 INV20 | DcMs_Amp_01 | A | 30.5.4026
SUINV20JB1 | 3 | DC current input 2 | SU F3 INV20 | DcMs_Amp_02 | A | 30.5.4027
SUINV20JB1 | 4 | DC current input 3 | SU F3 INV20 | DcMs_Amp_03 | A | 30.5.4028
SUINV20JB1 | 5 | DC current input 4 | SU F3 INV20 | DcMs_Amp_04 | A | 30.5.4029
SUINV20JB1 | 6 | DC current input 5 | SU F3 INV20 | DcMs_Amp_05 | A | 30.5.4030
SUINV20JB1 | 7 | DC current input 6 | SU F3 INV20 | DcMs_Amp_06 | A | 30.5.4031
SUINV20JB1 | 8 | DC current input 7 | SU F3 INV20 | DcMs_Amp_07 | A | 30.5.4032
SUINV20JB1 | 9 | DC current input 8 | SU F3 INV20 | DcMs_Amp_08 | A | 30.5.4033
SUINV20JB1 | 10 | DC current input 9 | SU F3 INV20 | DcMs_Amp_09 | A | 30.5.4034
SUINV20JB1 | 11 | DC current input 10 | SU F3 INV20 | DcMs_Amp_10 | A | 30.5.4035
SUINV20JB1 | 12 | DC current input 11 | SU F3 INV20 | DcMs_Amp_11 | A | 30.5.4036
SUINV20JB1 | 13 | DC current input 12 | SU F3 INV20 | DcMs_Amp_12 | A | 30.5.4037
SUINV20JB1 | 14 | DC current input 13 | SU F3 INV20 | DcMs_Amp_13 | A | 30.5.4038
SUINV20JB1 | 15 | DC current input 14 | SU F3 INV20 | DcMs_Amp_14 | A | 30.5.4039
SUINV20JB1 | 16 | DC current input 15 | SU F3 INV20 | DcMs_Amp_15 | A | 30.5.4040
SUINV20JB1 | 17 | DC current input 16 | SU F3 INV20 | DcMs_Amp_16 | A | 30.5.4041
SUINV20JB1 | 18 | DC current input 1 | SU F3 INV20 | DcMs_Amp_01_F | A | 30.5.4042
SUINV20JB1 | 19 | DC current input 2 | SU F3 INV20 | DcMs_Amp_02_F | A | 30.5.4043
SUINV20JB1 | 20 | DC current input 3 | SU F3 INV20 | DcMs_Amp_03_F | A | 30.5.4044
SUINV20JB1 | 21 | DC current input 4 | SU F3 INV20 | DcMs_Amp_04_F | A | 30.5.4045
SUINV20JB1 | 22 | DC current input 5 | SU F3 INV20 | DcMs_Amp_05_F | A | 30.5.4046
SUINV20JB1 | 23 | DC current input 6 | SU F3 INV20 | DcMs_Amp_06_F | A | 30.5.4047
SUINV20JB1 | 24 | DC current input 7 | SU F3 INV20 | DcMs_Amp_07_F | A | 30.5.4048
SUINV20JB1 | 25 | DC current input 8 | SU F3 INV20 | DcMs_Amp_08_F | A | 30.5.4049
SUINV20JB1 | 26 | DC current input 9 | SU F3 INV20 | DcMs_Amp_09_F | A | 30.5.4050
SUINV20JB1 | 27 | DC current input 10 | SU F3 INV20 | DcMs_Amp_10_F | A | 30.5.4051
SUINV20JB1 | 28 | DC current input 11 | SU F3 INV20 | DcMs_Amp_11_F | A | 30.5.4052
SUINV20JB1 | 29 | DC current input 12 | SU F3 INV20 | DcMs_Amp_12_F | A | 30.5.4053
SUINV20JB1 | 30 | DC current input 13 | SU F3 INV20 | DcMs_Amp_13_F | A | 30.5.4054
SUINV20JB1 | 31 | DC current input 14 | SU F3 INV20 | DcMs_Amp_14_F | A | 30.5.4055
SUINV20JB1 | 32 | DC current input 15 | SU F3 INV20 | DcMs_Amp_15_F | A | 30.5.4056
SUINV20JB1 | 33 | DC current input 16 | SU F3 INV20 | DcMs_Amp_16_F | A | 30.5.4057
SUINV20JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV20 | Dat_UpdCnt_1 | "-" | 30.5.4058
SUINV20JB2 | 2 | DC current input 1 | SU F3 INV20 | DcMs_Amp_01 | A | 30.5.4059
SUINV20JB2 | 3 | DC current input 2 | SU F3 INV20 | DcMs_Amp_02 | A | 30.5.4060
SUINV20JB2 | 4 | DC current input 3 | SU F3 INV20 | DcMs_Amp_03 | A | 30.5.4061
SUINV20JB2 | 5 | DC current input 4 | SU F3 INV20 | DcMs_Amp_04 | A | 30.5.4062
SUINV20JB2 | 6 | DC current input 5 | SU F3 INV20 | DcMs_Amp_05 | A | 30.5.4063
SUINV20JB2 | 7 | DC current input 6 | SU F3 INV20 | DcMs_Amp_06 | A | 30.5.4064
SUINV20JB2 | 8 | DC current input 7 | SU F3 INV20 | DcMs_Amp_07 | A | 30.5.4065
SUINV20JB2 | 9 | DC current input 8 | SU F3 INV20 | DcMs_Amp_08 | A | 30.5.4066
SUINV20JB2 | 10 | DC current input 9 | SU F3 INV20 | DcMs_Amp_09 | A | 30.5.4067
SUINV20JB2 | 11 | DC current input 10 | SU F3 INV20 | DcMs_Amp_10 | A | 30.5.4068
SUINV20JB2 | 12 | DC current input 11 | SU F3 INV20 | DcMs_Amp_11 | A | 30.5.4069
SUINV20JB2 | 13 | DC current input 12 | SU F3 INV20 | DcMs_Amp_12 | A | 30.5.4070
SUINV20JB2 | 14 | DC current input 13 | SU F3 INV20 | DcMs_Amp_13 | A | 30.5.4071
SUINV20JB2 | 15 | DC current input 14 | SU F3 INV20 | DcMs_Amp_14 | A | 30.5.4072
SUINV20JB2 | 16 | DC current input 15 | SU F3 INV20 | DcMs_Amp_15 | A | 30.5.4073
SUINV20JB2 | 17 | DC current input 16 | SU F3 INV20 | DcMs_Amp_16 | A | 30.5.4074
SUINV20JB2 | 18 | DC current input 1 | SU F3 INV20 | DcMs_Amp_01_F | A | 30.5.4075
SUINV20JB2 | 19 | DC current input 2 | SU F3 INV20 | DcMs_Amp_02_F | A | 30.5.4076
SUINV20JB2 | 20 | DC current input 3 | SU F3 INV20 | DcMs_Amp_03_F | A | 30.5.4077
SUINV20JB2 | 21 | DC current input 4 | SU F3 INV20 | DcMs_Amp_04_F | A | 30.5.4078
SUINV20JB2 | 22 | DC current input 5 | SU F3 INV20 | DcMs_Amp_05_F | A | 30.5.4079
SUINV20JB2 | 23 | DC current input 6 | SU F3 INV20 | DcMs_Amp_06_F | A | 30.5.4080
SUINV20JB2 | 24 | DC current input 7 | SU F3 INV20 | DcMs_Amp_07_F | A | 30.5.4081
SUINV20JB2 | 25 | DC current input 8 | SU F3 INV20 | DcMs_Amp_08_F | A | 30.5.4082
SUINV20JB2 | 26 | DC current input 9 | SU F3 INV20 | DcMs_Amp_09_F | A | 30.5.4083
SUINV20JB2 | 27 | DC current input 10 | SU F3 INV20 | DcMs_Amp_10_F | A | 30.5.4084
SUINV20JB2 | 28 | DC current input 11 | SU F3 INV20 | DcMs_Amp_11_F | A | 30.5.4085
SUINV20JB2 | 29 | DC current input 12 | SU F3 INV20 | DcMs_Amp_12_F | A | 30.5.4086
SUINV20JB2 | 30 | DC current input 13 | SU F3 INV20 | DcMs_Amp_13_F | A | 30.5.4087
SUINV20JB2 | 31 | DC current input 14 | SU F3 INV20 | DcMs_Amp_14_F | A | 30.5.4088
SUINV20JB2 | 32 | DC current input 15 | SU F3 INV20 | DcMs_Amp_15_F | A | 30.5.4089
SUINV20JB2 | 33 | DC current input 16 | SU F3 INV20 | DcMs_Amp_16_F | A | 30.5.4090
SUF3INV8 | 1 | DC voltage DC plus to DC minus | SU F3 INV8 | DcMs_Vol | V | 30.5.4091
SUF3INV8 | 2 | DC current inverter bridge 1 | SU F3 INV8 | DcMs_Amp_Stk1 | A | 30.5.4092
SUF3INV8 | 3 | DC current inverter bridge 2 | SU F3 INV8 | DcMs_Amp_Stk2 | A | 30.5.4093
SUF3INV8 | 4 | DC current inverter bridge 3 | SU F3 INV8 | DcMs_Amp_Stk3 | A | 30.5.4094
SUF3INV8 | 5 | DC current, total | SU F3 INV8 | DcMs_TotAmp | A | 30.5.4095
SUF3INV8 | 6 | DC power, total | SU F3 INV8 | DcMs_TotWatt | kW | 30.5.4096
SUF3INV8 | 7 | DC voltage of the inverter bridge 1 | SU F3 INV8 | InvMs_DclVol_Stk1 | V | 30.5.4097
SUF3INV8 | 8 | DC voltage of the inverter bridge 2 | SU F3 INV8 | InvMs_DclVol_Stk2 | V | 30.5.4098
SUF3INV8 | 9 | DC voltage of the inverter bridge 3 | SU F3 INV8 | InvMs_DclVol_Stk3 | V | 30.5.4099
SUF3INV8 | 10 | AC current L1, total | SU F3 INV8 | InvMs_TotA_PhsA | A | 30.5.4100
SUF3INV8 | 11 | AC current L2, total | SU F3 INV8 | InvMs_TotA_PhsB | A | 30.5.4101
SUF3INV8 | 12 | AC current L3, total | SU F3 INV8 | InvMs_TotA_PhsC | A | 30.5.4102
SUF3INV8 | 13 | Power factor (cos phi) | SU F3 INV8 | InvMs_PF | "-" | 30.5.4103
SUF3INV8 | 14 | Apparent power, total | SU F3 INV8 | InvMs_TotVA | kVA | 30.5.4104
SUF3INV8 | 15 | Active power, total | SU F3 INV8 | InvMs_TotW | kW | 30.5.4105
SUF3INV8 | 16 | Reactive power, total | SU F3 INV8 | InvMs_TotVAr | kVAr | 30.5.4106
SUF3INV8 | 17 | Line-to-line voltage L1-L2, utility grid | SU F3 INV8 | GriMs_V_PhsAB | V | 30.5.4107
SUF3INV8 | 18 | Line-to-line voltage L2-L3, utility grid | SU F3 INV8 | GriMs_V_PhsBC | V | 30.5.4108
SUF3INV8 | 19 | Line-to-line voltage L3-L1, utility grid | SU F3 INV8 | GriMs_V_PhsCA | V | 30.5.4109
SUF3INV8 | 20 | Power frequency | SU F3 INV8 | GriMs_Hz | Hz | 30.5.4110
SUF3INV8 | 21 | Temperature in the AC range | SU F3 INV8 | TmpCab_Acc | °C | 30.5.4111
SUF3INV8 | 22 | Temperature in the DC range | SU F3 INV8 | TmpCab_Dcc | °C | 30.5.4112
SUF3INV8 | 23 | Temperature in the electronics area | SU F3 INV8 | TmpCab_Rio | °C | 30.5.4113
SUF3INV8 | 24 | Temperature in interior, maximum value | SU F3 INV8 | TmpCab_Max | °C | 30.5.4114
SUF3INV8 | 25 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV8 | TmpStk_IgbtMax | °C | 30.5.4115
SUF3INV8 | 26 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV8 | TmpStk_PcbMax | °C | 30.5.4116
SUF3INV8 | 27 | Outside temperature | SU F3 INV8 | TmpExl | ?C | 30.5.4117
SUF3INV8 | 28 | Temperature of the MV transformer | SU F3 INV8 | TmpTrf | °C | 30.5.4118
SUF3INV8 | 29 | Switching status of the DC load-break switch 1 | SU F3 INV8 | DcSw1Stt | "-" | 30.5.4119
SUF3INV8 | 30 | Switching status of the DC load-break switch 2 | SU F3 INV8 | DcSw2Stt | "-" | 30.5.4120
SUF3INV8 | 31 | Switching status of the DC load-break switch 3 | SU F3 INV8 | DcSw3Stt | "-" | 30.5.4121
SUF3INV8 | 32 | Switching status of the AC circuit breaker | SU F3 INV8 | AcSwStt | "-" | 30.5.4122
SUF3INV8 | 33 | Switching state of the capacitor contactor | SU F3 INV8 | CapacSwStt | "-" | 30.5.4123
SUF3INV8 | 34 | Switching status of the pre-charging contactor | SU F3 INV8 | PrchrgSwStt | "-" | 30.5.4124
SUF3INV8 | 35 | Feed-in hours | SU F3 INV8 | Cnt_TotFeedTm | "-" | 30.5.4125
SUF3INV8 | 36 | Operating hours | SU F3 INV8 | Cnt_TotOpTm | "-" | 30.5.4126
SUF3INV8 | 37 | DC energy drawn, total | SU F3 INV8 | Cnt_TotWatthIn | MWh | 30.5.4127
SUF3INV8 | 38 | AC energy fed in, total | SU F3 INV8 | Cnt_TotWhOut | MWh | 30.5.4128
SUF3INV8 | 39 | DC energy drawn that day | SU F3 INV8 | Cnt_WatthIn | MWh | 30.5.4129
SUF3INV8 | 40 | AC energy fed in that day | SU F3 INV8 | Cnt_WhOut | MWh | 30.5.4130
SUF3INV8 | 41 | Operating hours of the interior fan 1 | SU F3 INV8 | Cnt_FanCab1Tm | "-" | 30.5.4131
SUF3INV8 | 42 | Operating hours of the interior fan 2 | SU F3 INV8 | Cnt_FanCab2Tm | "-" | 30.5.4132
SUF3INV8 | 43 | Operating hours of the inverter bridge fan | SU F3 INV8 | Cnt_FanStkTm | "-" | 30.5.4133
SUF3INV8 | 44 | Operating hours of the internal heating element | SU F3 INV8 | Cnt_HtCabTm | "-" | 30.5.4134
SUF3INV8 | 45 | Operating hours of the -40?C internal heating element | SU F3 INV8 | Cnt_HtLoExlTmpTm | "-" | 30.5.4135
SUF3INV8 | 46 | Error location of the present error | SU F3 INV8 | ErrLcn | "-" | 30.5.4136
SUF3INV8 | 47 | Error status of the inverter | SU F3 INV8 | ErrStt | "-" | 30.5.4137
SUF3INV8 | 48 | Error number of the present error | SU F3 INV8 | ErrNo | "-" | 30.5.4138
SUF3INV8 | 49 | Operating state of the inverter | SU F3 INV8 | OpStt | "-" | 30.5.4139
SUF3INV8 | 50 | Switch status of the start-stop key switch | SU F3 INV8 | Rio_KeySw | "-" | 30.5.4140
SUF3INV8 | 51 | Waiting time for grid connection | SU F3 INV8 | WaitGriTm | s | 30.5.4141
SUF3INV8 | 52 | Inverter serial number | SU F3 INV8 | DevInf_SerNo | "-" | 30.5.4142
SUF3INV8 | 53 | Switching status of the GFDI | SU F3 INV8 | GfdiSwStt | "-" | 30.5.4143
SUF3INV8 | 54 | Active power, setpoint | SU F3 INV8 | WSpt | kW | 30.5.4144
SUF3INV8 | 55 | Maximum apparent power, setpoint | SU F3 INV8 | VAMaxSpt | kVA | 30.5.4145
SUF3INV8 | 56 | Reactive power, setpoint | SU F3 INV8 | VArSpt | kVAr | 30.5.4146
SUF3INV8 | 57 | Power factor cos (phi), setpoint | SU F3 INV8 | PFSpt | "-" | 30.5.4147
SUF3INV8 | 58 | Fast stop hermetic protection, pressure | SU F3 INV8 | TrfPro_Pres | "-" | 30.5.4148
SUF3INV8 | 59 | Fast stop hermetic protection, temperature | SU F3 INV8 | TrfPro_TmpTrp | "-" | 30.5.4149
SUF3INV8 | 60 | Hermetic protection, gas fill level | SU F3 INV8 | TrfPro_GasOilLev | "-" | 30.5.4150
SUF3INV8 | 61 | Hermetic pressure, temperature warning | SU F3 INV8 | TrfPro_TmpWrn | "-" | 30.5.4151
SUF3INV8 | 62 | Temperature of inverter bridge 1 (switch) | SU F3 INV8 | TmpStk1_Igbt | °C | 30.5.4152
SUF3INV8 | 63 | Temperature of inverter bridge 2 (switch) | SU F3 INV8 | TmpStk2_Igbt | °C | 30.5.4153
SUF3INV8 | 64 | Temperature of inverter bridge 3 (switch) | SU F3 INV8 | TmpStk3_Igbt | °C | 30.5.4154
SUF3INV8 | 65 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV8 | TmpStk1_Pcb | ?C | 30.5.4155
SUF3INV8 | 66 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV8 | TmpStk2_Pcb | ?C | 30.5.4156
SUF3INV8 | 67 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV8 | TmpStk3_Pcb | ?C | 30.5.4157
SUF3INV8 | 68 | AC Energy Fed in the previous Day | SU F3 INV8 | Cnt_YstdWhOut | MWh | 30.5.4158
SUF3INV8 | 69 | CPU running time since system start | SU F3 INV8 | Cpu1UpTime | s | 30.5.4159
SUF3INV8 | 70 | Insulation resistance | SU F3 INV8 | PvGnd_RisIso | kOhm | 30.5.4160
SUF3INV8 | 71 | MV transformer pressure | SU F3 INV8 | PresTrf | "-" | 30.5.4161
SUF3INV8 | 72 | Error status of MV transformer pressure monitoring | SU F3 INV8 | PresTrf_ErrStt | "-" | 30.5.4162
SUF3INV8 | 73 | DC voltage DC plus to DC minus | SU F3 INV8 | DcMs_Vol_F | V | 30.5.4163
SUF3INV8 | 74 | DC current inverter bridge 1 | SU F3 INV8 | DcMs_Amp_Stk1_F | A | 30.5.4164
SUF3INV8 | 75 | DC current inverter bridge 2 | SU F3 INV8 | DcMs_Amp_Stk2_F | A | 30.5.4165
SUF3INV8 | 76 | DC current inverter bridge 3 | SU F3 INV8 | DcMs_Amp_Stk3_F | A | 30.5.4166
SUF3INV8 | 77 | DC current, total | SU F3 INV8 | DcMs_TotAmp_F | A | 30.5.4167
SUF3INV8 | 78 | DC power, total | SU F3 INV8 | DcMs_TotWatt_F | kW | 30.5.4168
SUF3INV8 | 79 | DC voltage of the inverter bridge 1 | SU F3 INV8 | InvMs_DclVol_Stk1_F | V | 30.5.4169
SUF3INV8 | 80 | DC voltage of the inverter bridge 2 | SU F3 INV8 | InvMs_DclVol_Stk2_F | V | 30.5.4170
SUF3INV8 | 81 | DC voltage of the inverter bridge 3 | SU F3 INV8 | InvMs_DclVol_Stk3_F | V | 30.5.4171
SUF3INV8 | 82 | AC current L1, total | SU F3 INV8 | InvMs_TotA_PhsA_F | A | 30.5.4172
SUF3INV8 | 83 | AC current L2, total | SU F3 INV8 | InvMs_TotA_PhsB_F | A | 30.5.4173
SUF3INV8 | 84 | AC current L3, total | SU F3 INV8 | InvMs_TotA_PhsC_F | A | 30.5.4174
SUF3INV8 | 85 | Power factor (cos phi) | SU F3 INV8 | InvMs_PF_F | "-" | 30.5.4175
SUF3INV8 | 86 | Active power, total | SU F3 INV8 | InvMs_TotW_F | kW | 30.5.4176
SUF3INV8 | 87 | Reactive power, total | SU F3 INV8 | InvMs_TotVAr_F | kVAr | 30.5.4177
SUF3INV8 | 88 | Line-to-line voltage L1-L2, utility grid | SU F3 INV8 | GriMs_V_PhsAB_F | V | 30.5.4178
SUF3INV8 | 89 | Line-to-line voltage L2-L3, utility grid | SU F3 INV8 | GriMs_V_PhsBC_F | V | 30.5.4179
SUF3INV8 | 90 | Line-to-line voltage L3-L1, utility grid | SU F3 INV8 | GriMs_V_PhsCA_F | V | 30.5.4180
SUF3INV8 | 91 | Power frequency | SU F3 INV8 | GriMs_Hz_F | Hz | 30.5.4181
SUF3INV8 | 92 | Temperature in the AC range | SU F3 INV8 | TmpCab_Acc_F | °C | 30.5.4182
SUF3INV8 | 93 | Temperature in the DC range | SU F3 INV8 | TmpCab_Dcc_F | °C | 30.5.4183
SUF3INV8 | 94 | Temperature in the electronics area | SU F3 INV8 | TmpCab_Rio_F | °C | 30.5.4184
SUF3INV8 | 95 | Temperature in interior, maximum value | SU F3 INV8 | TmpCab_Max_F | °C | 30.5.4185
SUF3INV8 | 96 | Temperature of the inverter bridge (switch), maximum value | SU F3 INV8 | TmpStk_IgbtMax_F | °C | 30.5.4186
SUF3INV8 | 97 | Temperature of the inverter bridge (assembly), maximum value | SU F3 INV8 | TmpStk_PcbMax_F | °C | 30.5.4187
SUF3INV8 | 98 | Outside temperature | SU F3 INV8 | TmpExl_F | ?C | 30.5.4188
SUF3INV8 | 99 | Temperature of the MV transformer | SU F3 INV8 | TmpTrf_F | °C | 30.5.4189
SUF3INV8 | 100 | Temperature of inverter bridge 1 (switch) | SU F3 INV8 | TmpStk1_Igbt_F | °C | 30.5.4190
SUF3INV8 | 101 | Temperature of inverter bridge 2 (switch) | SU F3 INV8 | TmpStk2_Igbt_F | °C | 30.5.4191
SUF3INV8 | 102 | Temperature of inverter bridge 3 (switch) | SU F3 INV8 | TmpStk3_Igbt_F | °C | 30.5.4192
SUF3INV8 | 103 | Maximum temperature of inverter bridge 1 (assembly) | SU F3 INV8 | TmpStk1_Pcb_F | ?C | 30.5.4193
SUF3INV8 | 104 | Maximum temperature of inverter bridge 2 (assembly) | SU F3 INV8 | TmpStk2_Pcb_F | ?C | 30.5.4194
SUF3INV8 | 105 | Maximum temperature of inverter bridge 3 (assembly) | SU F3 INV8 | TmpStk3_Pcb_F | ?C | 30.5.4195
SUF3INV8 | 106 | MV transformer pressure | SU F3 INV8 | PresTrf_F | "-" | 30.5.4196
SUF3INV8 | 110 | Switching status of the DC load-break switch | SU F3 INV8 | DcSwStt | "-" | 30.5.4197
SUINV8JB1 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV8 | Dat_UpdCnt_1 | "-" | 30.5.4198
SUINV8JB1 | 2 | DC current input 1 | SU F3 INV8 | DcMs_Amp_01 | A | 30.5.4199
SUINV8JB1 | 3 | DC current input 2 | SU F3 INV8 | DcMs_Amp_02 | A | 30.5.4200
SUINV8JB1 | 4 | DC current input 3 | SU F3 INV8 | DcMs_Amp_03 | A | 30.5.4201
SUINV8JB1 | 5 | DC current input 4 | SU F3 INV8 | DcMs_Amp_04 | A | 30.5.4202
SUINV8JB1 | 6 | DC current input 5 | SU F3 INV8 | DcMs_Amp_05 | A | 30.5.4203
SUINV8JB1 | 7 | DC current input 6 | SU F3 INV8 | DcMs_Amp_06 | A | 30.5.4204
SUINV8JB1 | 8 | DC current input 7 | SU F3 INV8 | DcMs_Amp_07 | A | 30.5.4205
SUINV8JB1 | 9 | DC current input 8 | SU F3 INV8 | DcMs_Amp_08 | A | 30.5.4206
SUINV8JB1 | 10 | DC current input 9 | SU F3 INV8 | DcMs_Amp_09 | A | 30.5.4207
SUINV8JB1 | 11 | DC current input 10 | SU F3 INV8 | DcMs_Amp_10 | A | 30.5.4208
SUINV8JB1 | 12 | DC current input 11 | SU F3 INV8 | DcMs_Amp_11 | A | 30.5.4209
SUINV8JB1 | 13 | DC current input 12 | SU F3 INV8 | DcMs_Amp_12 | A | 30.5.4210
SUINV8JB1 | 14 | DC current input 13 | SU F3 INV8 | DcMs_Amp_13 | A | 30.5.4211
SUINV8JB1 | 15 | DC current input 14 | SU F3 INV8 | DcMs_Amp_14 | A | 30.5.4212
SUINV8JB1 | 16 | DC current input 15 | SU F3 INV8 | DcMs_Amp_15 | A | 30.5.4213
SUINV8JB1 | 17 | DC current input 16 | SU F3 INV8 | DcMs_Amp_16 | A | 30.5.4214
SUINV8JB1 | 18 | DC current input 1 | SU F3 INV8 | DcMs_Amp_01_F | A | 30.5.4215
SUINV8JB1 | 19 | DC current input 2 | SU F3 INV8 | DcMs_Amp_02_F | A | 30.5.4216
SUINV8JB1 | 20 | DC current input 3 | SU F3 INV8 | DcMs_Amp_03_F | A | 30.5.4217
SUINV8JB1 | 21 | DC current input 4 | SU F3 INV8 | DcMs_Amp_04_F | A | 30.5.4218
SUINV8JB1 | 22 | DC current input 5 | SU F3 INV8 | DcMs_Amp_05_F | A | 30.5.4219
SUINV8JB1 | 23 | DC current input 6 | SU F3 INV8 | DcMs_Amp_06_F | A | 30.5.4220
SUINV8JB1 | 24 | DC current input 7 | SU F3 INV8 | DcMs_Amp_07_F | A | 30.5.4221
SUINV8JB1 | 25 | DC current input 8 | SU F3 INV8 | DcMs_Amp_08_F | A | 30.5.4222
SUINV8JB1 | 26 | DC current input 9 | SU F3 INV8 | DcMs_Amp_09_F | A | 30.5.4223
SUINV8JB1 | 27 | DC current input 10 | SU F3 INV8 | DcMs_Amp_10_F | A | 30.5.4224
SUINV8JB1 | 28 | DC current input 11 | SU F3 INV8 | DcMs_Amp_11_F | A | 30.5.4225
SUINV8JB1 | 29 | DC current input 12 | SU F3 INV8 | DcMs_Amp_12_F | A | 30.5.4226
SUINV8JB1 | 30 | DC current input 13 | SU F3 INV8 | DcMs_Amp_13_F | A | 30.5.4227
SUINV8JB1 | 31 | DC current input 14 | SU F3 INV8 | DcMs_Amp_14_F | A | 30.5.4228
SUINV8JB1 | 32 | DC current input 15 | SU F3 INV8 | DcMs_Amp_15_F | A | 30.5.4229
SUINV8JB1 | 33 | DC current input 16 | SU F3 INV8 | DcMs_Amp_16_F | A | 30.5.4230
SUINV8JB2 | 1 | Channel for monitoring of data transmission Left Zone | SU F3 INV8 | Dat_UpdCnt_1 | "-" | 30.5.4231
SUINV8JB2 | 2 | DC current input 1 | SU F3 INV8 | DcMs_Amp_01 | A | 30.5.4232
SUINV8JB2 | 3 | DC current input 2 | SU F3 INV8 | DcMs_Amp_02 | A | 30.5.4233
SUINV8JB2 | 4 | DC current input 3 | SU F3 INV8 | DcMs_Amp_03 | A | 30.5.4234
SUINV8JB2 | 5 | DC current input 4 | SU F3 INV8 | DcMs_Amp_04 | A | 30.5.4235
SUINV8JB2 | 6 | DC current input 5 | SU F3 INV8 | DcMs_Amp_05 | A | 30.5.4236
SUINV8JB2 | 7 | DC current input 6 | SU F3 INV8 | DcMs_Amp_06 | A | 30.5.4237
SUINV8JB2 | 8 | DC current input 7 | SU F3 INV8 | DcMs_Amp_07 | A | 30.5.4238
SUINV8JB2 | 9 | DC current input 8 | SU F3 INV8 | DcMs_Amp_08 | A | 30.5.4239
SUINV8JB2 | 10 | DC current input 9 | SU F3 INV8 | DcMs_Amp_09 | A | 30.5.4240
SUINV8JB2 | 11 | DC current input 10 | SU F3 INV8 | DcMs_Amp_10 | A | 30.5.4241
SUINV8JB2 | 12 | DC current input 11 | SU F3 INV8 | DcMs_Amp_11 | A | 30.5.4242
SUINV8JB2 | 13 | DC current input 12 | SU F3 INV8 | DcMs_Amp_12 | A | 30.5.4243
SUINV8JB2 | 14 | DC current input 13 | SU F3 INV8 | DcMs_Amp_13 | A | 30.5.4244
SUINV8JB2 | 15 | DC current input 14 | SU F3 INV8 | DcMs_Amp_14 | A | 30.5.4245
SUINV8JB2 | 16 | DC current input 15 | SU F3 INV8 | DcMs_Amp_15 | A | 30.5.4246
SUINV8JB2 | 17 | DC current input 16 | SU F3 INV8 | DcMs_Amp_16 | A | 30.5.4247
SUINV8JB2 | 18 | DC current input 1 | SU F3 INV8 | DcMs_Amp_01_F | A | 30.5.4248
SUINV8JB2 | 19 | DC current input 2 | SU F3 INV8 | DcMs_Amp_02_F | A | 30.5.4249
SUINV8JB2 | 20 | DC current input 3 | SU F3 INV8 | DcMs_Amp_03_F | A | 30.5.4250
SUINV8JB2 | 21 | DC current input 4 | SU F3 INV8 | DcMs_Amp_04_F | A | 30.5.4251
SUINV8JB2 | 22 | DC current input 5 | SU F3 INV8 | DcMs_Amp_05_F | A | 30.5.4252
SUINV8JB2 | 23 | DC current input 6 | SU F3 INV8 | DcMs_Amp_06_F | A | 30.5.4253
SUINV8JB2 | 24 | DC current input 7 | SU F3 INV8 | DcMs_Amp_07_F | A | 30.5.4254
SUINV8JB2 | 25 | DC current input 8 | SU F3 INV8 | DcMs_Amp_08_F | A | 30.5.4255
SUINV8JB2 | 26 | DC current input 9 | SU F3 INV8 | DcMs_Amp_09_F | A | 30.5.4256
SUINV8JB2 | 27 | DC current input 10 | SU F3 INV8 | DcMs_Amp_10_F | A | 30.5.4257
SUINV8JB2 | 28 | DC current input 11 | SU F3 INV8 | DcMs_Amp_11_F | A | 30.5.4258
SUINV8JB2 | 29 | DC current input 12 | SU F3 INV8 | DcMs_Amp_12_F | A | 30.5.4259
SUINV8JB2 | 30 | DC current input 13 | SU F3 INV8 | DcMs_Amp_13_F | A | 30.5.4260
SUINV8JB2 | 31 | DC current input 14 | SU F3 INV8 | DcMs_Amp_14_F | A | 30.5.4261
SUINV8JB2 | 32 | DC current input 15 | SU F3 INV8 | DcMs_Amp_15_F | A | 30.5.4262
SUINV8JB2 | 33 | DC current input 16 | SU F3 INV8 | DcMs_Amp_16_F | A | 30.5.4263
SUKPIPLNT | 1 | DC Input Corrected | SU KPI PLNT | DcINCorr | V | 30.5.4264
SUKPIPLNT | 2 | Module Temperature CF | SU KPI PLNT | ModTempCF | A | 30.5.4265
SUKPIPLNT | 3 | Other Causes CF | SU KPI PLNT | OthCF | A | 30.5.4266
SUKPIPLNT | 4 | Ratio Corrected | SU KPI PLNT | RatioCorr | A | 30.5.4267
SUKPIPLNT | 5 | Ratio Module Temp CF | SU KPI PLNT | RatioCF | A | 30.5.4268
SUKPIPLNT | 6 | Ratio | SU KPI PLNT | Ratio | kW | 30.5.4269
SUMET1 | 1 | PVMET 330S Air Temp | SU MET 1 | Air_Temp | °C | 30.5.4270
SUMET1 | 2 | PVMET 330S Relative Humididy | SU MET 1 | Rel_Humididy | % | 30.5.4271
SUMET1 | 3 | PVMET 330S Barometric Pressure | SU MET 1 | Bar_Pressure | hPa | 30.5.4272
SUMET1 | 4 | PVMET 330S Wind Speed | SU MET 1 | Wind_Speed | m/s | 30.5.4273
SUMET1 | 5 | PVMET 330S Wind dir | SU MET 1 | Wind_Dir |  | 30.5.4274
SUMET1 | 6 | PVMET 330S Wind Gust | SU MET 1 | Wind_Gust | m/s | 30.5.4275
SUMET1 | 7 | PVMET 330S Wind Gust Dir | SU MET 1 | Wind_Gust_Dir |  | 30.5.4276
SUMET1 | 8 | PVMET 330S Rainfall | SU MET 1 | Rainfall |  | 30.5.4277
SUMET1 | 9 | PVMET 330S BOM Temp1 | SU MET 1 | BOM_Temp1 | °C | 30.5.4278
SUMET1 | 10 | PVMET 330S BOM Temp2 | SU MET 1 | BOM_Temp2 | °C | 30.5.4279
SUMET1 | 11 | PVMET 150S Global Irradiance | SU MET 1 | Glob_Irradiance | W/m2 | 30.5.4280
SUMET1 | 12 | PVMET 150S Irradiance POA | SU MET 1 | POA_Irr | W/m2 | 30.5.4281
SUMET1 | 16 | PVMET 150S Global Sens Const | SU MET 1 | Glob_Sens | uV/W | 30.5.4282
SUMET1 | 17 | PVMET 150S POA Sens Const | SU MET 1 | POA_Sens | uV/W | 30.5.4283
SUMET1 | 18 | SI RS485 Irradiance | SU MET 1 | Irradiance | W/m2 | 30.5.4284
SUMET1 | 19 | SI RS485 Cell Temp | SU MET 1 | Cell_Temp | °C | 30.5.4285
SUMET1 | 21 | PVMET 330S Air Temp filt | SU MET 1 | Air_Temp_F | °C | 30.5.4286
SUMET1 | 22 | PVMET 330S Relative Humididy filt | SU MET 1 | Rel_Humididy_F | % | 30.5.4287
SUMET1 | 23 | PVMET 330S Barometric Pressure filt | SU MET 1 | Bar_Pressure_F | hPa | 30.5.4288
SUMET1 | 24 | PVMET 330S Wind Speed filt | SU MET 1 | Wind_Speed_F | m/s | 30.5.4289
SUMET1 | 25 | PVMET 330S Wind dir filt | SU MET 1 | Wind_Dir_F |  | 30.5.4290
SUMET1 | 26 | PVMET 330S Wind Gust filt | SU MET 1 | Wind_Gust_F | m/s | 30.5.4291
SUMET1 | 27 | PVMET 330S Wind Gust Dir filt | SU MET 1 | Wind_Gust_Dir_F | m/s | 30.5.4292
SUMET1 | 28 | PVMET 330S Rainfall filt | SU MET 1 | Rainfall_F |  | 30.5.4293
SUMET1 | 29 | PVMET 330S BOM Temp1 filt | SU MET 1 | BOM_Temp1_F | °C | 30.5.4294
SUMET1 | 30 | PVMET 330S BOM Temp2 filt | SU MET 1 | BOM_Temp2_F | °C | 30.5.4295
SUMET1 | 31 | PVMET 150S Global Irradiance filt | SU MET 1 | Glob_Irradiance_F | W/m2 | 30.5.4296
SUMET1 | 32 | PVMET 150S Irradiance POA filt | SU MET 1 | POA_Irr_F | W/m2 | 30.5.4297
SUMET1 | 33 | PVMET 150S Air Temp filt | SU MET 1 | Air_Temp_F | °C | 30.5.4298
SUMET1 | 34 | PVMET 150S BOM Temp1 filt | SU MET 1 | BOM_Temp1_F | °C | 30.5.4299
SUMET1 | 35 | PVMET 150S BOM Temp1 filt | SU MET 1 | BOM_Temp1_F | °C | 30.5.4300
SUMET1 | 36 | PVMET 150S Global Sens Const filt | SU MET 1 | Glob_Send_F | uV/W | 30.5.4301
SUMET1 | 37 | PVMET 150S POA Sens Const | SU MET 1 | POA_Sens_F | uv/W | 30.5.4302
SUMET1 | 38 | SI RS485 Irradiance | SU MET 1 | Irradiance_F | W/m2 | 30.5.4303
SUMET1 | 39 | SI RS485 Cell Temp | SU MET 1 | Cell_Temp_F | °C | 30.5.4304
SUMET1 | 40 | Calc - Irradiance at STC | SU MET 1 | STCIrrMET |  | 30.5.4305
SUMET1 | 41 | Calc - Module Temp at STC | SU MET 1 | STCModTmpMET | °C | 30.5.4306
SUMET1 | 42 | Calc - Module Temp at NOTC | SU MET 1 | NOCTModTmpMET | °C | 30.5.4307
SUMET1 | 43 | Calc - Minimum Irradiance | SU MET 1 | MinIrrMET |  | 30.5.4308
SUMET1 | 44 | Calc - Pyranometer Irrad(equiv) | SU MET 1 | rmsVPOI |  | 30.5.4309
SUMET1 | 45 | Module Temp (extimated with Tamb) | SU MET 1 | extModTmpMET | °C | 30.5.4310
SUMET2 | 1 | PVMET 330S Air Temp | SU MET 2 | Air_Temp | °C | 30.5.4311
SUMET2 | 2 | PVMET 330S Relative Humididy | SU MET 2 | Rel_Humididy | % | 30.5.4312
SUMET2 | 3 | PVMET 330S Barometric Pressure | SU MET 2 | Bar_Pressure | hPa | 30.5.4313
SUMET2 | 4 | PVMET 330S Wind Speed | SU MET 2 | Wind_Speed | m/s | 30.5.4314
SUMET2 | 5 | PVMET 330S Wind dir | SU MET 2 | Wind_Dir |  | 30.5.4315
SUMET2 | 6 | PVMET 330S Wind Gust | SU MET 2 | Wind_Gust | m/s | 30.5.4316
SUMET2 | 7 | PVMET 330S Wind Gust Dir | SU MET 2 | Wind_Gust_Dir |  | 30.5.4317
SUMET2 | 8 | PVMET 330S Rainfall | SU MET 2 | Rainfall |  | 30.5.4318
SUMET2 | 9 | PVMET 330S BOM Temp1 | SU MET 2 | BOM_Temp1 | °C | 30.5.4319
SUMET2 | 10 | PVMET 330S BOM Temp2 | SU MET 2 | BOM_Temp2 | °C | 30.5.4320
SUMET2 | 11 | PVMET 150S Global Irradiance | SU MET 2 | Glob_Irradiance | W/m2 | 30.5.4321
SUMET2 | 12 | PVMET 150S Irradiance POA | SU MET 2 | POA_Irr | W/m2 | 30.5.4322
SUMET2 | 16 | PVMET 150S Global Sens Const | SU MET 2 | Glob_Sens | uV/W | 30.5.4323
SUMET2 | 17 | PVMET 150S POA Sens Const | SU MET 2 | POA_Sens | uV/W | 30.5.4324
SUMET2 | 18 | SI RS485 Irradiance | SU MET 2 | Irradiance | W/m2 | 30.5.4325
SUMET2 | 19 | SI RS485 Cell Temp | SU MET 2 | Cell_Temp | °C | 30.5.4326
SUMET2 | 21 | PVMET 330S Air Temp filt | SU MET 2 | Air_Temp_F | °C | 30.5.4327
SUMET2 | 22 | PVMET 330S Relative Humididy filt | SU MET 2 | Rel_Humididy_F | % | 30.5.4328
SUMET2 | 23 | PVMET 330S Barometric Pressure filt | SU MET 2 | Bar_Pressure_F | hPa | 30.5.4329
SUMET2 | 24 | PVMET 330S Wind Speed filt | SU MET 2 | Wind_Speed_F | m/s | 30.5.4330
SUMET2 | 25 | PVMET 330S Wind dir filt | SU MET 2 | Wind_Dir_F |  | 30.5.4331
SUMET2 | 26 | PVMET 330S Wind Gust filt | SU MET 2 | Wind_Gust_F | m/s | 30.5.4332
SUMET2 | 27 | PVMET 330S Wind Gust Dir filt | SU MET 2 | Wind_Gust_Dir_F | m/s | 30.5.4333
SUMET2 | 28 | PVMET 330S Rainfall filt | SU MET 2 | Rainfall_F |  | 30.5.4334
SUMET2 | 29 | PVMET 330S BOM Temp1 filt | SU MET 2 | BOM_Temp1_F | °C | 30.5.4335
SUMET2 | 30 | PVMET 330S BOM Temp2 filt | SU MET 2 | BOM_Temp2_F | °C | 30.5.4336
SUMET2 | 31 | PVMET 150S Global Irradiance filt | SU MET 2 | Glob_Irradiance_F | W/m2 | 30.5.4337
SUMET2 | 32 | PVMET 150S Irradiance POA filt | SU MET 2 | POA_Irr_F | W/m2 | 30.5.4338
SUMET2 | 33 | PVMET 150S Air Temp filt | SU MET 2 | Air_Temp_F | °C | 30.5.4339
SUMET2 | 34 | PVMET 150S BOM Temp1 filt | SU MET 2 | BOM_Temp1_F | °C | 30.5.4340
SUMET2 | 35 | PVMET 150S BOM Temp1 filt | SU MET 2 | BOM_Temp1_F | °C | 30.5.4341
SUMET2 | 36 | PVMET 150S Global Sens Const filt | SU MET 2 | Glob_Send_F | uV/W | 30.5.4342
SUMET2 | 37 | PVMET 150S POA Sens Const | SU MET 2 | POA_Sens_F | uv/W | 30.5.4343
SUMET2 | 38 | SI RS485 Irradiance | SU MET 2 | Irradiance_F | W/m2 | 30.5.4344
SUMET2 | 39 | SI RS485 Cell Temp | SU MET 2 | Cell_Temp_F | °C | 30.5.4345
SUMET2 | 40 | Calc - Irradiance at STC | SU MET 2 | STCIrrMET |  | 30.5.4346
SUMET2 | 41 | Calc - Module Temp at STC | SU MET 2 | STCModTmpMET | °C | 30.5.4347
SUMET2 | 42 | Calc - Module Temp at NOTC | SU MET 2 | NOCTModTmpMET | °C | 30.5.4348
SUMET2 | 43 | Calc - Minimum Irradiance | SU MET 2 | MinIrrMET |  | 30.5.4349
SUMET2 | 44 | Calc - Pyranometer Irrad(equiv) | SU MET 2 | rmsVPOI |  | 30.5.4350
SUMET2 | 45 | Module Temp (extimated with Tamb) | SU MET 2 | extModTmpMET | °C | 30.5.4351
SUMET3 | 1 | PVMET 330S Air Temp | SU MET 3 | Air_Temp | °C | 30.5.4352
SUMET3 | 2 | PVMET 330S Relative Humididy | SU MET 3 | Rel_Humididy | % | 30.5.4353
SUMET3 | 3 | PVMET 330S Barometric Pressure | SU MET 3 | Bar_Pressure | hPa | 30.5.4354
SUMET3 | 4 | PVMET 330S Wind Speed | SU MET 3 | Wind_Speed | m/s | 30.5.4355
SUMET3 | 5 | PVMET 330S Wind dir | SU MET 3 | Wind_Dir |  | 30.5.4356
SUMET3 | 6 | PVMET 330S Wind Gust | SU MET 3 | Wind_Gust | m/s | 30.5.4357
SUMET3 | 7 | PVMET 330S Wind Gust Dir | SU MET 3 | Wind_Gust_Dir |  | 30.5.4358
SUMET3 | 8 | PVMET 330S Rainfall | SU MET 3 | Rainfall |  | 30.5.4359
SUMET3 | 9 | PVMET 330S BOM Temp1 | SU MET 3 | BOM_Temp1 | °C | 30.5.4360
SUMET3 | 10 | PVMET 330S BOM Temp2 | SU MET 3 | BOM_Temp2 | °C | 30.5.4361
SUMET3 | 11 | PVMET 150S Global Irradiance | SU MET 3 | Glob_Irradiance | W/m2 | 30.5.4362
SUMET3 | 12 | PVMET 150S Irradiance POA | SU MET 3 | POA_Irr | W/m2 | 30.5.4363
SUMET3 | 16 | PVMET 150S Global Sens Const | SU MET 3 | Glob_Sens | uV/W | 30.5.4364
SUMET3 | 17 | PVMET 150S POA Sens Const | SU MET 3 | POA_Sens | uV/W | 30.5.4365
SUMET3 | 18 | SI RS485 Irradiance | SU MET 3 | Irradiance | W/m2 | 30.5.4366
SUMET3 | 19 | SI RS485 Cell Temp | SU MET 3 | Cell_Temp | °C | 30.5.4367
SUMET3 | 21 | PVMET 330S Air Temp filt | SU MET 3 | Air_Temp_F | °C | 30.5.4368
SUMET3 | 22 | PVMET 330S Relative Humididy filt | SU MET 3 | Rel_Humididy_F | % | 30.5.4369
SUMET3 | 23 | PVMET 330S Barometric Pressure filt | SU MET 3 | Bar_Pressure_F | hPa | 30.5.4370
SUMET3 | 24 | PVMET 330S Wind Speed filt | SU MET 3 | Wind_Speed_F | m/s | 30.5.4371
SUMET3 | 25 | PVMET 330S Wind dir filt | SU MET 3 | Wind_Dir_F |  | 30.5.4372
SUMET3 | 26 | PVMET 330S Wind Gust filt | SU MET 3 | Wind_Gust_F | m/s | 30.5.4373
SUMET3 | 27 | PVMET 330S Wind Gust Dir filt | SU MET 3 | Wind_Gust_Dir_F | m/s | 30.5.4374
SUMET3 | 28 | PVMET 330S Rainfall filt | SU MET 3 | Rainfall_F |  | 30.5.4375
SUMET3 | 29 | PVMET 330S BOM Temp1 filt | SU MET 3 | BOM_Temp1_F | °C | 30.5.4376
SUMET3 | 30 | PVMET 330S BOM Temp2 filt | SU MET 3 | BOM_Temp2_F | °C | 30.5.4377
SUMET3 | 31 | PVMET 150S Global Irradiance filt | SU MET 3 | Glob_Irradiance_F | W/m2 | 30.5.4378
SUMET3 | 32 | PVMET 150S Irradiance POA filt | SU MET 3 | POA_Irr_F | W/m2 | 30.5.4379
SUMET3 | 33 | PVMET 150S Air Temp filt | SU MET 3 | Air_Temp_F | °C | 30.5.4380
SUMET3 | 34 | PVMET 150S BOM Temp1 filt | SU MET 3 | BOM_Temp1_F | °C | 30.5.4381
SUMET3 | 35 | PVMET 150S BOM Temp1 filt | SU MET 3 | BOM_Temp1_F | °C | 30.5.4382
SUMET3 | 36 | PVMET 150S Global Sens Const filt | SU MET 3 | Glob_Send_F | uV/W | 30.5.4383
SUMET3 | 37 | PVMET 150S POA Sens Const | SU MET 3 | POA_Sens_F | uv/W | 30.5.4384
SUMET3 | 38 | SI RS485 Irradiance | SU MET 3 | Irradiance_F | W/m2 | 30.5.4385
SUMET3 | 39 | SI RS485 Cell Temp | SU MET 3 | Cell_Temp_F | °C | 30.5.4386
SUMET3 | 40 | Calc - Irradiance at STC | SU MET 3 | STCIrrMET |  | 30.5.4387
SUMET3 | 41 | Calc - Module Temp at STC | SU MET 3 | STCModTmpMET | °C | 30.5.4388
SUMET3 | 42 | Calc - Module Temp at NOTC | SU MET 3 | NOCTModTmpMET | °C | 30.5.4389
SUMET3 | 43 | Calc - Minimum Irradiance | SU MET 3 | MinIrrMET |  | 30.5.4390
SUMET3 | 44 | Calc - Pyranometer Irrad(equiv) | SU MET 3 | rmsVPOI |  | 30.5.4391
SUMET3 | 45 | Module Temp (extimated with Tamb) | SU MET 3 | extModTmpMET | °C | 30.5.4392
SUMET4 | 1 | PVMET 330S Air Temp | SU MET 4 | Air_Temp | °C | 30.5.4393
SUMET4 | 2 | PVMET 330S Relative Humididy | SU MET 4 | Rel_Humididy | % | 30.5.4394
SUMET4 | 3 | PVMET 330S Barometric Pressure | SU MET 4 | Bar_Pressure | hPa | 30.5.4395
SUMET4 | 4 | PVMET 330S Wind Speed | SU MET 4 | Wind_Speed | m/s | 30.5.4396
SUMET4 | 5 | PVMET 330S Wind dir | SU MET 4 | Wind_Dir |  | 30.5.4397
SUMET4 | 6 | PVMET 330S Wind Gust | SU MET 4 | Wind_Gust | m/s | 30.5.4398
SUMET4 | 7 | PVMET 330S Wind Gust Dir | SU MET 4 | Wind_Gust_Dir |  | 30.5.4399
SUMET4 | 8 | PVMET 330S Rainfall | SU MET 4 | Rainfall |  | 30.5.4400
SUMET4 | 9 | PVMET 330S BOM Temp1 | SU MET 4 | BOM_Temp1 | °C | 30.5.4401
SUMET4 | 10 | PVMET 330S BOM Temp2 | SU MET 4 | BOM_Temp2 | °C | 30.5.4402
SUMET4 | 11 | PVMET 150S Global Irradiance | SU MET 4 | Glob_Irradiance | W/m2 | 30.5.4403
SUMET4 | 12 | PVMET 150S Irradiance POA | SU MET 4 | POA_Irr | W/m2 | 30.5.4404
SUMET4 | 16 | PVMET 150S Global Sens Const | SU MET 4 | Glob_Sens | uV/W | 30.5.4405
SUMET4 | 17 | PVMET 150S POA Sens Const | SU MET 4 | POA_Sens | uV/W | 30.5.4406
SUMET4 | 18 | SI RS485 Irradiance | SU MET 4 | Irradiance | W/m2 | 30.5.4407
SUMET4 | 19 | SI RS485 Cell Temp | SU MET 4 | Cell_Temp | °C | 30.5.4408
SUMET4 | 21 | PVMET 330S Air Temp filt | SU MET 4 | Air_Temp_F | °C | 30.5.4409
SUMET4 | 22 | PVMET 330S Relative Humididy filt | SU MET 4 | Rel_Humididy_F | % | 30.5.4410
SUMET4 | 23 | PVMET 330S Barometric Pressure filt | SU MET 4 | Bar_Pressure_F | hPa | 30.5.4411
SUMET4 | 24 | PVMET 330S Wind Speed filt | SU MET 4 | Wind_Speed_F | m/s | 30.5.4412
SUMET4 | 25 | PVMET 330S Wind dir filt | SU MET 4 | Wind_Dir_F |  | 30.5.4413
SUMET4 | 26 | PVMET 330S Wind Gust filt | SU MET 4 | Wind_Gust_F | m/s | 30.5.4414
SUMET4 | 27 | PVMET 330S Wind Gust Dir filt | SU MET 4 | Wind_Gust_Dir_F | m/s | 30.5.4415
SUMET4 | 28 | PVMET 330S Rainfall filt | SU MET 4 | Rainfall_F |  | 30.5.4416
SUMET4 | 29 | PVMET 330S BOM Temp1 filt | SU MET 4 | BOM_Temp1_F | °C | 30.5.4417
SUMET4 | 30 | PVMET 330S BOM Temp2 filt | SU MET 4 | BOM_Temp2_F | °C | 30.5.4418
SUMET4 | 31 | PVMET 150S Global Irradiance filt | SU MET 4 | Glob_Irradiance_F | W/m2 | 30.5.4419
SUMET4 | 32 | PVMET 150S Irradiance POA filt | SU MET 4 | POA_Irr_F | W/m2 | 30.5.4420
SUMET4 | 33 | PVMET 150S Air Temp filt | SU MET 4 | Air_Temp_F | °C | 30.5.4421
SUMET4 | 34 | PVMET 150S BOM Temp1 filt | SU MET 4 | BOM_Temp1_F | °C | 30.5.4422
SUMET4 | 35 | PVMET 150S BOM Temp1 filt | SU MET 4 | BOM_Temp1_F | °C | 30.5.4423
SUMET4 | 36 | PVMET 150S Global Sens Const filt | SU MET 4 | Glob_Send_F | uV/W | 30.5.4424
SUMET4 | 37 | PVMET 150S POA Sens Const | SU MET 4 | POA_Sens_F | uv/W | 30.5.4425
SUMET4 | 38 | SI RS485 Irradiance | SU MET 4 | Irradiance_F | W/m2 | 30.5.4426
SUMET4 | 39 | SI RS485 Cell Temp | SU MET 4 | Cell_Temp_F | °C | 30.5.4427
SUMET4 | 40 | Calc - Irradiance at STC | SU MET 4 | STCIrrMET |  | 30.5.4428
SUMET4 | 41 | Calc - Module Temp at STC | SU MET 4 | STCModTmpMET | °C | 30.5.4429
SUMET4 | 42 | Calc - Module Temp at NOTC | SU MET 4 | NOCTModTmpMET | °C | 30.5.4430
SUMET4 | 43 | Calc - Minimum Irradiance | SU MET 4 | MinIrrMET |  | 30.5.4431
SUMET4 | 44 | Calc - Pyranometer Irrad(equiv) | SU MET 4 | rmsVPOI |  | 30.5.4432
SUMET4 | 45 | Module Temp (extimated with Tamb) | SU MET 4 | extModTmpMET | °C | 30.5.4433
SUMETAVG | 1 | PVMET 330S Air Temp | SU MET AVG | Air_Temp | °C | 30.5.4434
SUMETAVG | 2 | PVMET 330S Relative Humididy | SU MET AVG | Rel_Humididy | % | 30.5.4435
SUMETAVG | 3 | PVMET 330S Barometric Pressure | SU MET AVG | Bar_Pressure | hPa | 30.5.4436
SUMETAVG | 4 | PVMET 330S Wind Speed | SU MET AVG | Wind_Speed | m/s | 30.5.4437
SUMETAVG | 5 | PVMET 330S Wind dir | SU MET AVG | Wind_Dir |  | 30.5.4438
SUMETAVG | 6 | PVMET 330S Wind Gust | SU MET AVG | Wind_Gust | m/s | 30.5.4439
SUMETAVG | 7 | PVMET 330S Wind Gust Dir | SU MET AVG | Wind_Gust_Dir |  | 30.5.4440
SUMETAVG | 8 | PVMET 330S Rainfall | SU MET AVG | Rainfall |  | 30.5.4441
SUMETAVG | 9 | PVMET 330S BOM Temp1 | SU MET AVG | BOM_Temp1 | °C | 30.5.4442
SUMETAVG | 10 | PVMET 330S BOM Temp2 | SU MET AVG | BOM_Temp2 | °C | 30.5.4443
SUMETAVG | 11 | PVMET 150S Global Irradiance | SU MET AVG | Glob_Irradiance | W/m2 | 30.5.4444
SUMETAVG | 12 | PVMET 150S Irradiance POA | SU MET AVG | POA_Irr | W/m2 | 30.5.4445
SUMETAVG | 13 | PVMET 150S Air Temp | SU MET AVG | Air_Temp | °C | 30.5.4446
SUMETAVG | 14 | PVMET 150S BOM Temp1 | SU MET AVG | BOM_Temp1 | °C | 30.5.4447
SUMETAVG | 15 | PVMET 150S BOM Temp1 | SU MET AVG | BOM_Temp1 | °C | 30.5.4448
SUMETAVG | 16 | PVMET 150S Global Sens Const | SU MET AVG | Glob_Send | uV/W | 30.5.4449
SUMETAVG | 17 | PVMET 150S POA Sens Const | SU MET AVG | POA_Sens | uv/W | 30.5.4450
SUMETAVG | 18 | SI RS485 Irradiance | SU MET AVG | Irradiance | W/m2 | 30.5.4451
SUMETAVG | 19 | SI RS485 Cell Temp | SU MET AVG | Cell_Temp | °C | 30.5.4452
SUMETAVG | 21 | PVMET 330S Air Temp filt | SU MET AVG | Air_Temp_F | °C | 30.5.4453
SUMETAVG | 22 | PVMET 330S Relative Humididy filt | SU MET AVG | Rel_Humididy_F | % | 30.5.4454
SUMETAVG | 23 | PVMET 330S Barometric Pressure filt | SU MET AVG | Bar_Pressure_F | hPa | 30.5.4455
SUMETAVG | 24 | PVMET 330S Wind Speed filt | SU MET AVG | Wind_Speed_F | m/s | 30.5.4456
SUMETAVG | 25 | PVMET 330S Wind dir filt | SU MET AVG | Wind_Dir_F |  | 30.5.4457
SUMETAVG | 26 | PVMET 330S Wind Gust filt | SU MET AVG | Wind_Gust_F | m/s | 30.5.4458
SUMETAVG | 27 | PVMET 330S Wind Gust Dir filt | SU MET AVG | Wind_Gust_Dir_F | m/s | 30.5.4459
SUMETAVG | 28 | PVMET 330S Rainfall filt | SU MET AVG | Rainfall_F |  | 30.5.4460
SUMETAVG | 29 | PVMET 330S BOM Temp1 filt | SU MET AVG | BOM_Temp1_F | °C | 30.5.4461
SUMETAVG | 30 | PVMET 330S BOM Temp2 filt | SU MET AVG | BOM_Temp2_F | °C | 30.5.4462
SUMETAVG | 31 | PVMET 150S Global Irradiance filt | SU MET AVG | Glob_Irradiance_F | W/m2 | 30.5.4463
SUMETAVG | 32 | PVMET 150S Irradiance POA filt | SU MET AVG | POA_Irr_F | W/m2 | 30.5.4464
SUMETAVG | 33 | PVMET 150S Air Temp filt | SU MET AVG | Air_Temp_F | °C | 30.5.4465
SUMETAVG | 34 | PVMET 150S BOM Temp1 filt | SU MET AVG | BOM_Temp1_F | °C | 30.5.4466
SUMETAVG | 35 | PVMET 150S BOM Temp1 filt | SU MET AVG | BOM_Temp1_F | °C | 30.5.4467
SUMETAVG | 36 | PVMET 150S Global Sens Const filt | SU MET AVG | Glob_Send_F | uV/W | 30.5.4468
SUMETAVG | 37 | PVMET 150S POA Sens Const | SU MET AVG | POA_Sens_F | uv/W | 30.5.4469
SUMETAVG | 38 | SI RS485 Irradiance | SU MET AVG | Irradiance_F | W/m2 | 30.5.4470
SUMETAVG | 39 | SI RS485 Cell Temp | SU MET AVG | Cell_Temp_F | °C | 30.5.4471
SUMETAVG | 40 | Calc - Irradiance at STC | SU MET AVG | STCIrrMET |  | 30.5.4472
SUMETAVG | 41 | Calc - Module Temp at STC | SU MET AVG | STCModTmpMET | °C | 30.5.4473
SUMETAVG | 42 | Calc - Module Temp at NOTC | SU MET AVG | NOCTModTmpMET | °C | 30.5.4474
SUMETAVG | 43 | Calc - Minimum Irradiance | SU MET AVG | MinIrrMET |  | 30.5.4475
SUMETAVG | 44 | Calc - Pyranometer Irrad(equiv) | SU MET AVG | rmsVPOI |  | 30.5.4476
SUMETAVG | 45 | Module Temp (extimated with Tamb) | SU MET AVG | extModTmpMET | °C | 30.5.4477
SUPLNTCNTR | 2 | Active Power Process Variable | SU PLNT CNTR | PPVPC | MW | 30.5.4478
SUPLNTCNTR | 4 | Q Process Variable | SU PLNT CNTR | QPVPC | MVar | 30.5.4479
SUPLNTCNTR | 6 | V Process Variable | SU PLNT CNTR | VPVPC | kV | 30.5.4480
SUPLNTCNTR | 8 | PF Process Variable | SU PLNT CNTR | PFPVPC |  | 30.5.4481
SUPLNTCNTR | 41 | Read Ac Power SetPoint from Oper | SU PLNT CNTR | ReadPOperSetPC | MW | 30.5.4482
SUPLNTCNTR | 43 | Read React Power Set Point from Oper | SU PLNT CNTR | ReadQOperPC | MVar | 30.5.4483
SUPLNTCNTR | 45 | Read Voltage Set Point from Operator | SU PLNT CNTR | ReadVoperPC | kV | 30.5.4484
SUPLNTCNTR | 47 | Read Power Factor Set Point from Oper | SU PLNT CNTR | ReadPFOperPC |  | 30.5.4485
SUPLNTINV1 | 2 | Active Power Process Variable | SU PLNT INV1 | PPVPCInv | kW | 30.5.4486
SUPLNTINV1 | 4 | Reactive Power Process Variable | SU PLNT INV1 | QPVPCInv | kVar | 30.5.4487
SUPLNTINV1 | 41 | Read Active Power Inverter Set Point | SU PLNT INV1 | ReadPOperSetPCINV |  | 30.5.4488
SUPLNTINV1 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV1 | ReadQOperSetPCINV |  | 30.5.4489
SUPLNTINV10 | 2 | Active Power Process Variable | SU PLNT INV10 | PPVPCInv | kW | 30.5.4490
SUPLNTINV10 | 4 | Reactive Power Process Variable | SU PLNT INV10 | QPVPCInv | kVar | 30.5.4491
SUPLNTINV10 | 41 | Read Active Power Inverter Set Point | SU PLNT INV10 | ReadPOperSetPCINV |  | 30.5.4492
SUPLNTINV10 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV10 | ReadQOperSetPCINV |  | 30.5.4493
SUPLNTINV11 | 2 | Active Power Process Variable | SU PLNT INV11 | PPVPCInv | kW | 30.5.4494
SUPLNTINV11 | 4 | Reactive Power Process Variable | SU PLNT INV11 | QPVPCInv | kVar | 30.5.4495
SUPLNTINV11 | 41 | Read Active Power Inverter Set Point | SU PLNT INV11 | ReadPOperSetPCINV |  | 30.5.4496
SUPLNTINV11 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV11 | ReadQOperSetPCINV |  | 30.5.4497
SUPLNTINV12 | 2 | Active Power Process Variable | SU PLNT INV12 | PPVPCInv | kW | 30.5.4498
SUPLNTINV12 | 4 | Reactive Power Process Variable | SU PLNT INV12 | QPVPCInv | kVar | 30.5.4499
SUPLNTINV12 | 41 | Read Active Power Inverter Set Point | SU PLNT INV12 | ReadPOperSetPCINV |  | 30.5.4500
SUPLNTINV12 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV12 | ReadQOperSetPCINV |  | 30.5.4501
SUPLNTINV13 | 2 | Active Power Process Variable | SU PLNT INV13 | PPVPCInv | kW | 30.5.4502
SUPLNTINV13 | 4 | Reactive Power Process Variable | SU PLNT INV13 | QPVPCInv | kVar | 30.5.4503
SUPLNTINV13 | 41 | Read Active Power Inverter Set Point | SU PLNT INV13 | ReadPOperSetPCINV |  | 30.5.4504
SUPLNTINV13 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV13 | ReadQOperSetPCINV |  | 30.5.4505
SUPLNTINV14 | 2 | Active Power Process Variable | SU PLNT INV14 | PPVPCInv | kW | 30.5.4506
SUPLNTINV14 | 4 | Reactive Power Process Variable | SU PLNT INV14 | QPVPCInv | kVar | 30.5.4507
SUPLNTINV14 | 41 | Read Active Power Inverter Set Point | SU PLNT INV14 | ReadPOperSetPCINV |  | 30.5.4508
SUPLNTINV14 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV14 | ReadQOperSetPCINV |  | 30.5.4509
SUPLNTINV15 | 2 | Active Power Process Variable | SU PLNT INV15 | PPVPCInv | kW | 30.5.4510
SUPLNTINV15 | 4 | Reactive Power Process Variable | SU PLNT INV15 | QPVPCInv | kVar | 30.5.4511
SUPLNTINV15 | 41 | Read Active Power Inverter Set Point | SU PLNT INV15 | ReadPOperSetPCINV |  | 30.5.4512
SUPLNTINV15 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV15 | ReadQOperSetPCINV |  | 30.5.4513
SUPLNTINV16 | 2 | Active Power Process Variable | SU PLNT INV16 | PPVPCInv | kW | 30.5.4514
SUPLNTINV16 | 4 | Reactive Power Process Variable | SU PLNT INV16 | QPVPCInv | kVar | 30.5.4515
SUPLNTINV16 | 41 | Read Active Power Inverter Set Point | SU PLNT INV16 | ReadPOperSetPCINV |  | 30.5.4516
SUPLNTINV16 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV16 | ReadQOperSetPCINV |  | 30.5.4517
SUPLNTINV17 | 2 | Active Power Process Variable | SU PLNT INV17 | PPVPCInv | kW | 30.5.4518
SUPLNTINV17 | 4 | Reactive Power Process Variable | SU PLNT INV17 | QPVPCInv | kVar | 30.5.4519
SUPLNTINV17 | 41 | Read Active Power Inverter Set Point | SU PLNT INV17 | ReadPOperSetPCINV |  | 30.5.4520
SUPLNTINV17 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV17 | ReadQOperSetPCINV |  | 30.5.4521
SUPLNTINV18 | 2 | Active Power Process Variable | SU PLNT INV18 | PPVPCInv | kW | 30.5.4522
SUPLNTINV18 | 4 | Reactive Power Process Variable | SU PLNT INV18 | QPVPCInv | kVar | 30.5.4523
SUPLNTINV18 | 41 | Read Active Power Inverter Set Point | SU PLNT INV18 | ReadPOperSetPCINV |  | 30.5.4524
SUPLNTINV18 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV18 | ReadQOperSetPCINV |  | 30.5.4525
SUPLNTINV19 | 2 | Active Power Process Variable | SU PLNT INV19 | PPVPCInv | kW | 30.5.4526
SUPLNTINV19 | 4 | Reactive Power Process Variable | SU PLNT INV19 | QPVPCInv | kVar | 30.5.4527
SUPLNTINV19 | 41 | Read Active Power Inverter Set Point | SU PLNT INV19 | ReadPOperSetPCINV |  | 30.5.4528
SUPLNTINV19 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV19 | ReadQOperSetPCINV |  | 30.5.4529
SUPLNTINV2 | 2 | Active Power Process Variable | SU PLNT INV2 | PPVPCInv | kW | 30.5.4530
SUPLNTINV2 | 4 | Reactive Power Process Variable | SU PLNT INV2 | QPVPCInv | kVar | 30.5.4531
SUPLNTINV2 | 41 | Read Active Power Inverter Set Point | SU PLNT INV2 | ReadPOperSetPCINV | kW | 30.5.4532
SUPLNTINV2 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV2 | ReadQOperSetPCINV | kVar | 30.5.4533
SUPLNTINV20 | 2 | Active Power Process Variable | SU PLNT INV20 | PPVPCInv | kW | 30.5.4534
SUPLNTINV20 | 4 | Reactive Power Process Variable | SU PLNT INV20 | QPVPCInv | kVar | 30.5.4535
SUPLNTINV20 | 41 | Read Active Power Inverter Set Point | SU PLNT INV20 | ReadPOperSetPCINV |  | 30.5.4536
SUPLNTINV20 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV20 | ReadQOperSetPCINV |  | 30.5.4537
SUPLNTINV21 | 2 | Active Power Process Variable | SU PLNT INV21 | PPVPCInv | kW | 30.5.4538
SUPLNTINV21 | 4 | Reactive Power Process Variable | SU PLNT INV21 | QPVPCInv | kVar | 30.5.4539
SUPLNTINV21 | 41 | Read Active Power Inverter Set Point | SU PLNT INV21 | ReadPOperSetPCINV |  | 30.5.4540
SUPLNTINV21 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV21 | ReadQOperSetPCINV |  | 30.5.4541
SUPLNTINV22 | 2 | Active Power Process Variable | SU PLNT INV22 | PPVPCInv | kW | 30.5.4542
SUPLNTINV22 | 4 | Reactive Power Process Variable | SU PLNT INV22 | QPVPCInv | kVar | 30.5.4543
SUPLNTINV22 | 41 | Read Active Power Inverter Set Point | SU PLNT INV22 | ReadPOperSetPCINV |  | 30.5.4544
SUPLNTINV22 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV22 | ReadQOperSetPCINV |  | 30.5.4545
SUPLNTINV23 | 2 | Active Power Process Variable | SU PLNT INV23 | PPVPCInv | kW | 30.5.4546
SUPLNTINV23 | 4 | Reactive Power Process Variable | SU PLNT INV23 | QPVPCInv | kVar | 30.5.4547
SUPLNTINV23 | 41 | Read Active Power Inverter Set Point | SU PLNT INV23 | ReadPOperSetPCINV |  | 30.5.4548
SUPLNTINV23 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV23 | ReadQOperSetPCINV |  | 30.5.4549
SUPLNTINV3 | 2 | Active Power Process Variable | SU PLNT INV3 | PPVPCInv | kW | 30.5.4550
SUPLNTINV3 | 4 | Reactive Power Process Variable | SU PLNT INV3 | QPVPCInv | kVar | 30.5.4551
SUPLNTINV3 | 41 | Read Active Power Inverter Set Point | SU PLNT INV3 | ReadPOperSetPCINV |  | 30.5.4552
SUPLNTINV3 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV3 | ReadQOperSetPCINV |  | 30.5.4553
SUPLNTINV4 | 2 | Active Power Process Variable | SU PLNT INV4 | PPVPCInv | kW | 30.5.4554
SUPLNTINV4 | 4 | Reactive Power Process Variable | SU PLNT INV4 | QPVPCInv | kVar | 30.5.4555
SUPLNTINV4 | 41 | Read Active Power Inverter Set Point | SU PLNT INV4 | ReadPOperSetPCINV |  | 30.5.4556
SUPLNTINV4 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV4 | ReadQOperSetPCINV |  | 30.5.4557
SUPLNTINV5 | 2 | Active Power Process Variable | SU PLNT INV5 | PPVPCInv | kW | 30.5.4558
SUPLNTINV5 | 4 | Reactive Power Process Variable | SU PLNT INV5 | QPVPCInv | kVar | 30.5.4559
SUPLNTINV5 | 41 | Read Active Power Inverter Set Point | SU PLNT INV5 | ReadPOperSetPCINV |  | 30.5.4560
SUPLNTINV5 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV5 | ReadQOperSetPCINV |  | 30.5.4561
SUPLNTINV6 | 2 | Active Power Process Variable | SU PLNT INV6 | PPVPCInv | kW | 30.5.4562
SUPLNTINV6 | 4 | Reactive Power Process Variable | SU PLNT INV6 | QPVPCInv | kVar | 30.5.4563
SUPLNTINV6 | 41 | Read Active Power Inverter Set Point | SU PLNT INV6 | ReadPOperSetPCINV |  | 30.5.4564
SUPLNTINV6 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV6 | ReadQOperSetPCINV |  | 30.5.4565
SUPLNTINV7 | 2 | Active Power Process Variable | SU PLNT INV7 | PPVPCInv | kW | 30.5.4566
SUPLNTINV7 | 4 | Reactive Power Process Variable | SU PLNT INV7 | QPVPCInv | kVar | 30.5.4567
SUPLNTINV7 | 41 | Read Active Power Inverter Set Point | SU PLNT INV7 | ReadPOperSetPCINV |  | 30.5.4568
SUPLNTINV7 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV7 | ReadQOperSetPCINV |  | 30.5.4569
SUPLNTINV8 | 2 | Active Power Process Variable | SU PLNT INV8 | PPVPCInv | kW | 30.5.4570
SUPLNTINV8 | 4 | Reactive Power Process Variable | SU PLNT INV8 | QPVPCInv | kVar | 30.5.4571
SUPLNTINV8 | 41 | Read Active Power Inverter Set Point | SU PLNT INV8 | ReadPOperSetPCINV |  | 30.5.4572
SUPLNTINV8 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV8 | ReadQOperSetPCINV |  | 30.5.4573
SUPLNTINV9 | 2 | Active Power Process Variable | SU PLNT INV9 | PPVPCInv | kW | 30.5.4574
SUPLNTINV9 | 4 | Reactive Power Process Variable | SU PLNT INV9 | QPVPCInv | kVar | 30.5.4575
SUPLNTINV9 | 41 | Read Active Power Inverter Set Point | SU PLNT INV9 | ReadPOperSetPCINV |  | 30.5.4576
SUPLNTINV9 | 43 | Read Reactive Power Inverter Set Point | SU PLNT INV9 | ReadQOperSetPCINV |  | 30.5.4577
SUPOI | 1 | POI Active Power | SU POI | WPOI | MW | 30.5.4578
SUPOI | 2 | POI Reactive Power | SU POI | VArPOI | MVar | 30.5.4579
SUPOI | 3 | POI Power Factor | SU POI | PFPOI |  | 30.5.4580
SUPOI | 4 | POI Frequency | SU POI | HzPOI | Hz | 30.5.4581
SUPOI | 5 | POI Linear Voltage U12 | SU POI | U12VPOI |  | 30.5.4582
SUPOI | 6 | POI Linear Voltage U23 | SU POI | U21VPOI |  | 30.5.4583
SUPOI | 7 | POI Linear Voltage U31 | SU POI | U31VPOI |  | 30.5.4584
SUPOI | 8 | POI Phase Current L1 | SU POI | L1APOI |  | 30.5.4585
SUPOI | 9 | POI Phase Current L2 | SU POI | L2APOI |  | 30.5.4586
SUPOI | 10 | POI Phase Current L3 | SU POI | L3APOI |  | 30.5.4587
SUPOI | 11 | POI Linear Voltage rms | SU POI | rmsVPOI | kV | 30.5.4588
SUPOI | 12 | POI Current rms | SU POI | rmsAPOI | A | 30.5.4589
SUPOI | 13 | POI Active Power filt | SU POI | WPOI_F |  | 30.5.4590
SUPOI | 14 | POI Reactive Power filt | SU POI | VArPOI_F |  | 30.5.4591
SUPOI | 15 | POI Power Factor filt | SU POI | PFPOI_F |  | 30.5.4592
SUPOI | 16 | Calc - Energy at POI dt 15 min | SU POI | EEdt15POI |  | 30.5.4593
SUPOI | 134 | Reactive Power Low Side TR | SU POI | Reactive Power | MVAr | 30.5.4594
SUPPD | 1 | Number of Inverters Start up | SU PPD | StartCntPPD |  | 30.5.4595
SUPPD | 2 | Number of Inverters in Production | SU PPD | ProdCntPPD |  | 30.5.4596
SUPPD | 3 | Number of Inverters stopped | SU PPD | StopCntPPD |  | 30.5.4597
SUPPD | 4 | Number of Inverters in fault | SU PPD | FaultCntPPD |  | 30.5.4598
SUPPD | 5 | Number of Inverters in Local | SU PPD | LocCntPPD |  | 30.5.4599
SUPPD | 6 | Number of Inverters in Limitation | SU PPD | LimCntPPD |  | 30.5.4600
SUPPD | 7 | Number of Inverters in P Manual | SU PPD | PManPPD |  | 30.5.4601
SUPPD | 8 | Number of Inverters in Q Manual | SU PPD | QManCntPPD |  | 30.5.4602
SUPPD | 13 | ActivePowerSum | SU PPD | PActPPD |  | 30.5.4603
SUPPD | 14 | Plant Nominal Active Power | SU PPD | PActNomPPD |  | 30.5.4604
SUPPD | 15 | Inverter Nominal Active Power (AC) | SU PPD | PActInvNomACPPD |  | 30.5.4605
SUPPD | 16 | Inverter Nominal Power (DC) | SU PPD | PActInvNomDCPPD |  | 30.5.4606
SUPPD | 17 | Total Plant Number of Inverters | SU PPD | NumInvPPD |  | 30.5.4607
SUPPD | 18 | Total Plant Number of modules | SU PPD | NumInvModPPD |  | 30.5.4608
SUPPD | 19 | Plant Status | SU PPD | StPPD |  | 30.5.4609
SUPPD | 20 | Plant Operation | SU PPD | OpPPD |  | 30.5.4610
SUPPD | 21 | Performance Ratio (Plant) | SU PPD | PRPPD |  | 30.5.4611
SUPPD | 22 | Performance Ratio Corrected (Plant) | SU PPD | PRCorPPD |  | 30.5.4612
SUPPD | 23 | Performance Ratio Mod TempCF(Plant) | SU PPD | PRvsTmodPPD |  | 30.5.4613
SUPPD | 24 | Energy at DC in Corrected (Plant) | SU PPD | EE_DCCorrPPD |  | 30.5.4614
SUPPD | 25 | Energy Module Temp CF (Plant) | SU PPD | EE_EvsTmodPPD |  | 30.5.4615
SUPPD | 26 | Energy Other causes CF (Plant) | SU PPD | EE_EvsOthPPD |  | 30.5.4616
METEO_CALIB | 1 | Global Sensitivity Constant Indication |  | Global Sensitivity Constant Indication |  | 30.5.4617
METEO_CALIB | 3 | POA Sensitivity Constant Indication |  | POA Sensitivity Constant Indication |  | 30.5.4618
SYS_NETD | 3 | NET 3 Diagnostics |  |  |  | 30.5.4619